## Instrument
ITEM# | PLANT | PART | SYS | SYS # | ISA ID | EQ | EQ # | COM. | Item Ref | TAG NUMBER | INSTRUMENT TYPE | PART OF PLANT | SYSTEM | Associated EquiP # | Associated Equip Description | Parameter | Line Number | LINE SIZE (mm) | LINE SPEC (Note 5) | Service | Press Min | Press Max | Temp. Min | Temp. Max | Flow Min | Flow max | UNITS | INSTRUMENT RANGE | OPERATING VALUE | CALIBRATED RANGE | INSTALLATION DRAWING (TABG-JEC-0-000-) | DATASHEET / Reference (TABG-JEC-0-000-) | P&ID (TABG-JEC-0-000-) | NOTES | REV | VENDOR | MAKE | MODEL | PO | RCVD | FailSafe
261 | TH00 | 011 | 0LFC | 10 | LIT | CL | 010 |  | 38 | 0110LFC10CL010 | Level Transmitter (Radar) | Wellpad TH11 | Common Steam/Water Dump System | - | Wellpad Pond | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 2200 to 6000 | - | 2200 to 6000 | CCI-DET-2706 CCI-DET-2711 | CCI-DAT-1468 | PRO-PID-0033 | Bracket Mount | 7.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
257 | TH00 | 011 | 0NAB | 10 | FIT | DF | 010 |  | 34 | 0110NAB10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH11 | Condensate System | - | Well TH11 | Flow | 0110NAB10-BR010-300-S12 | 300 | S12 | Condensate | Full Vac | 23 | -5 | 215 | 0 | 1399 | tph | -10 to 1399 | 550 | 0 to 1399T/H 0 to 621.3mb | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0033 | Notes 3, Note 4, Note 8 | 7.8 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ | 4500191995 | 2023-02-13
260 | TH00 | 011 | 0NAB | 10 | PIT | CP | 010 |  | 37 | 0110NAB10CP010 | Pressure Indicating Transmitter | Wellpad TH11 | Condensate System | - | Well TH11 | Pressure | N/A | 3 1/8" | S12 | Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 5.1 | 0 to 25 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0033 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
259 | TH00 | 011 | 0NAB | 10 | PI | CP | 510 |  | 36 | 0110NAB10CP510 | Pressure Gauge | Wellpad TH11 | Condensate System | - | Well TH11 | Pressure | N/A | 3 1/8" | S12 | Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | 0 to 25 | 5.1 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0033 |  | 3.2 | Wika | Wika | 72039878+14503369+0731277 | 4500189704 | 2022-11-10
258 | TH00 | 011 | 0NAB | 10 | PI | CP | 520 |  | 35 | 0110NAB10CP520 | Pressure Gauge | Wellpad TH11 | Condensate System | - | Well TH11 FCV Inlet | Pressure | 0110NAB10-BR010-300-S12 | 300 | S12 | Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | 0 to 60 | 5.1 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0033 |  | 7.3 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
299 | TH00 | 012 | 0LFC | 10 | LIT | CL | 010 |  | 80 | 0120LFC10CL010 | Level Transmitter (Radar) | Wellpad TH12 | Common Steam/Water Dump System | 0120LFC10-BB010 | Silencer | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 0 to 1300 | 950 | 0 to 1300 | (LFC-)MEC-AGT-2099 | CCI-DAT-1468 | PRO-PID-0037 | Bracket Mount, Vee-notch weirbox level | 3.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
300 | test | 012 | 0LFC | 10 | LIT | CL | 010 |  | 80 | testLFC10CL010 | Level Transmitter (Radar) | Wellpad TH12 | Common Steam/Water Dump System | 0120LFC10-BB010 | test-silenced | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 0 to 1300 | 950 | 0 to 1300 | (LFC-)MEC-AGT-2099 | CCI-DAT-1468 | PRO-PID-0037 | Bracket Mount, Vee-notch weirbox level | 3.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10

## Well
Service Properties
General Notes:
1. Two-Phase flow calculation undertaken in control system with DP and Static pressure instrument process variable signals from instrument.
2. CEL to provide orifice plate sizing for two-phase flow meter.
3. Flow element to be conditioning type to minimize upstream and downstream straight lengths.
4. Reverse flow detection required for reinjection flow transmitters.
5. For Pipe Specification Information Refer to TABG-JEC-0-000-PRO-PID-0002.
6. Flanged instruments shall be ASME B16.5 unless otherwise specified.
7. Wake frequency calculations to be performed for all thermowells and corrosometers. Instrument vendor to confirm insertion length based on calculations and pipe dimension.
8. Square root extraction within DP instrument to output linearised flow measurement.

## SEP
Service Properties
General Notes:
1. Supplied with Equipment. To be confirmed with equipment Supplier.
2. SIL rated instrument with yellow coloured body.
3. Flow element to be conditioning type to minimize upstream and downstream straight lengths.
4. -
5. For Pipe Specification Information Refer to TABG-JEC-0-000-PRO-PID-0002.
6. Flanged instruments shall be ASME B16.5 unless otherwise specified.
7. Wake frequency calculations to be performed for all thermowells and corrosometers. Instrument vendor to confirm insertion length based on calculations and pipe dimension.
8. Square root extraction within DP instrument to output linearised flow measurement output.

## SGW
Service Properties
General Notes:
1. Supplied with Equipment. To be confirmed with equipment Supplier.
2. -
3. Flow element to be conditioning type to minimize upstream and downstream straight lengths.
4. -
5. For Pipe Specification Information Refer to TABG-JEC-0-000-PRO-PID-0002.
6. Flanged instruments shall be ASME B16.5 unless otherwise specified.
7. Wake frequency calculations to be performed for all thermowells. Instrument vendor to confirm insertion length based on calculations and pipe dimension.
8. Square root extraction within DP instrument to output linearised flow measurement output.