## C&I Devices
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14 | Column15 | Column16 | Column17 | Column18 | Column19 | Column20 | Column21 | Column22 | Column23 | Column24 | Column25 | Column26 | Column27 | Column28 | Column29 | Column30 | Column31 | Column32 | Column33 | Column34 | Column35 | Column36 | Column37 | Column38 | Column39 | Column40 | Column41 | Column42 | Column43 | Column44 | Column45 | Column46 | Column47 | Column48 | Column49 | Column50 | Column51 | Column52 | Column53 | Column54 | Column55 | Column56 | Column57
Station | System | Tag | Point |  | Funct | Type | Range | ResCon | PECPR | KPI | Setting | NominalValue | Proof | MVUnit | MVar1 | MVar2 | MVar3 | MVar4 | MVar5 | MVar6 | MVar7 | IdealUnit | IdO1 | IdO2 | IdO3 | IdO4 | IdO5 | IdO6 | IdO7 | Digi1 | Digi2 | Digi3 | Digi4 | Digi5 | Digi6 | DeviceType | Procs | Criticality | ResCon | PECPR | KPI | PlantCode | Data (CCI-DAT-) | StoresNo | DrawingNo | Checked | DateChecked | CheckedBy | Changed | CalcErr
Te Mihi | U1 Component Cooling Water | 10CL001 (50) | CCW EXPANSION TANK LEVEL (50) | 29 | Alarm & Indication | ABB 266DSHGSSA2B1-L5-B2-I2(50) | 0 - 1400 mmH2O |  |  |  | 0 - 1400 mmH2O |  |  | mmH2O | 0.00 | 350 | 700 | 1050 | 1400 | 0.01 |  | mA | Column24 IdO1: 4; Column25 IdO2: 8; Column26 IdO3: 12; Column27 IdO4: 16; Column28 IdO5: 20; Column31 Digi1: 840; Column32 Digi2: 1260 | 60 | TconTHI1.Hardware.0.11.504 appTHI1Unit1.aiTHIG0010PGB10CL001. LRV=410, URV=1810mmH2O. | C |  | no | no | 10PGB10CL001 | (255) | (50) | X-PGB-ME-PID-101[F2] & 1-CRA-IC-LPD-504.4[G4](50) | TRUE | 2014-05-26 | R Fear | TRUE | TRUE
station | system | tag | point | 5 | - | type | range |  |  |  | 2200 to 6000 | - | 6000 | mm | 2200 | 3150 | 4100 | 5050 | 6000 | 0 |  | mA | Column24 IdO1: 4; Column25 IdO2: 8; Column26 IdO3: 12; Column27 IdO4: 16; Column28 IdO5: 20; Column31 Digi1: 500 | Level Transmitter (Radar) | TH11-7.5.001-01 | C |  |  |  | 0110LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-33

## Battery Systems
Installed Battery Systems Data Entry Sheet
Station | System | Use | Bank Vtge | Cells | Banks | Make | Type | Battery Vtge | A/H | Disch A | Disch Hrs | Disch Final Vpc | Last Discharge | Comments
Tauhara | TH11 | Motorised valves, power supply, communication | 121 VDC | 54 | 1 | Enersys | Lead Acid SuperSafeTM | 2.26 VDC | 5 AH |  |  |  |  | TABG-JEC-0-000-ELE-DAT-1032_1 110VDC - Data Sheet - Well Pad VALVE REGULATED LEAD-ACID 100% TH11-1010-01_1_STEAMFIELD WELLPAD TH11 110VDC
Tauhara | TH12 | Motorised valves, power supply, communication | 121 VDC | 54 | 1 | Enersys | Lead Acid SuperSafeTM | 2.26 VDC | 5 AH |  |  |  |  | TABG-JEC-0-000-ELE-DAT-1032_1 110VDC - Data Sheet - Well Pad VALVE REGULATED LEAD-ACID 100% TH12-1010-01_1.1_STEAMFIELD WELLPAD TH12 110VDC
Tauhara | TH26 | Motorised valves, power supply, communication | 121 VDC | 54 | 1 | Enersys | Lead Acid SuperSafeTM | 2.26 VDC | 5 AH |  |  |  |  | TABG-JEC-0-000-ELE-DAT-1032_1 110VDC - Data Sheet - Well Pad VALVE REGULATED LEAD-ACID 100% TH26-1010-01_1_STEAMFIELD WELLPAD TH26 110VDC
Tauhara | TH28 | Motorised valves, power supply, communication | 121 VDC | 54 | 1 | Enersys | Lead Acid SuperSafeTM | 2.26 VDC | 5 AH |  |  |  |  | TABG-JEC-0-000-ELE-DAT-1032_1 110VDC - Data Sheet - Well Pad VALVE REGULATED LEAD-ACID 100% TH28-1010-01_1_STEAMFIELD WELLPAD TH28 110VDC
Tauhara | TH29 | Motorised valves, power supply, communication | 121 VDC | 54 | 1 | Enersys | Lead Acid SuperSafeTM | 2.26 VDC | 5 AH |  |  |  |  | TABG-JEC-0-000-ELE-DAT-1032_1 110VDC - Data Sheet - Well Pad VALVE REGULATED LEAD-ACID 100% TH29-1010-01_1_STEAMFIELD WELLPAD TH29 110VDC
Tauhara | TH37 | Motorised valves, power supply, communication | 121 VDC | 54 | 1 | Enersys | Lead Acid SuperSafeTM | 2.26 VDC | 5 AH |  |  |  |  | TABG-JEC-0-000-ELE-DAT-1032_1 110VDC - Data Sheet - Well Pad VALVE REGULATED LEAD-ACID 100% TH37-1010-01_1_STEAMFIELD WELLPAD TH37 110VDC
Tauhara | SEP Plant | Power supply, PLC IO, UPS/Inverter communication | 121 VDC | 54 | 2 | Enersys | Lead Acid SuperSafeTM | 2.26 VDC | 350 AH |  |  |  |  | TABG-JEC-0-000-ELE-DAT-1031 VALVE REGULATED LEAD-ACID 100% TABG-JEC-0-BFC-ELE-SLD-2330_1 SP 110VDC SLD
Tauhara | SGW Pump Station | Power supply, PLC IO, UPS/Inverter communication | 121 VDC | 54 | 2 | Enersys | Lead Acid SuperSafeTM | 2.26 VDC | 375 AH |  |  |  |  | TABG-JEC-0-000-ELE-DAT-1031 VALVE REGULATED LEAD-ACID 100% 110VDC TABG-JEC-0-BFC-ELE-SLD-1330_1 SGW 110VDC SLD

## Transformers
Transformer Data Entry Sheet - Including Oil Analysis & DGA Test Requirements
STATION | TFMR | HT | LT | MVA | SYSTEM | TYPE | ANNUAL OIL TEST | OVERHAUL | DOBLE | OIL VOLUME | SERIAL NO | NOTES
Tauhara | P020BFE10GT010 | 11kV | 690V | 2 | SGW | Delta/Star | [5 empty] | SGW Re-injection pump A transformer
Tauhara | P020BFE10GT020 | 11kV | 690V | 2 | SGW | Delta/Star | [5 empty] | SGW Re-injection pump B transformer
Tauhara | P020BFE10GT030 | 11kV | 690V | 2 | SGW | Delta/Star | [5 empty] | SGW Re-injection pump C transformer
Tauhara | S020BFT10GT010 | 11kV | 400V | 0.75 | SEP Plant | Delta/Star | [5 empty] | SEP Plant 400V switch board Local services transformer 1 TABG-JEC-0-000-ELE-SLD-2300_1_SP LV SLD Incomer
Tauhara | S020BFT10GT020 | 11kV | 400V | 0.75 | SEP Plant | Delta/Star | [5 empty] | SEP Plant 400V switch board Local services transformer 2 TABG-JEC-0-000-ELE-SLD-2300_1_SP LV SLD Incomer
Tauhara | P020BFT10GT010 | 11kV | 400V | 2 | SGW | Delta/Star | [5 empty] | SGW 400V Switcboard Local services transformer 1 TABG-JEC-0-000-ELE-SLD-1300_1_ SGW LV SLD Incomer
Tauhara | P020BFT10GT020 | 11kV | 400V | 2 | SGW | Delta/Star | [5 empty] | SGW 400V Switcboard Local services transformer 2 TABG-JEC-0-000-ELE-SLD-1300_1_ SGW LV SLD Incomer
Tauhara | [11 empty] | Pole mounted transformer for TH11

## Rotable Plant Item
Rotable Plant Data Entry Sheet - Rotable items not permanently assigned to a KKS location
System | Serial Number | Type | Date | Location | Details | Notes

## Electrical Equipment
Electrical Equipment Data Entry Sheet - includes Motors, Actuators, Control Valves etc. Does not include CB's or Transformers
Station | System | Equipment | Description | Make | Model | Type | Rating | Notes | KKS Code
P020BFE10GU010_-M01 |  | Motor | SGW PUMP A VSD COOLANT PUMP MOTOR
P020BFE10GU020_-M01 |  | Motor | SGW PUMP B VSD COOLANT PUMP MOTOR
P020BFE10GU030_-M01 |  | Motor | SGW PUMP C VSD COOLANT PUMP MOTOR
P020GWA20AP020_-M01 |  | Motor | Seal water bund sump pump motor
P020GWB10AP010_-M01 |  | Motor | GFHP Seal Water Pump A Motor
P020GWB10AP020_-M01 |  | Motor | GFHP Seal Water Pump B Motor
P020GWA22AP010_-M01 |  | Motor | Seal Water Supply Pump A Motor
P020GWA22AP020_-M01 |  | Motor | Seal Water Supply Pump B Motor
P020GWA22AP030_-M01 |  | Motor | Seal Water Supply Pump C Motor
P020GWA30AH010_-M01 |  | Motor | Seal Water Return Fin Fan Cooler Motor 1
P020GWA30AH010_M02 |  | Motor | Seal Water Return Fin Fan Cooler Motor 2
P020LFC20AP010_-M01 |  | Motor | GEOTHERMAL FLUID HOLDING POND (GFHP) PUMP A Motor
P020LFC20AP020_-M01 |  | Motor | GEOTHERMAL FLUID HOLDING POND (GFHP) PUMP B Motor
P020NAB10AP010_-M01 |  | Motor | Condensate Pump A Motor
P020NAB10AP020_-M01 |  | Motor | Condensate pump B Motor
P020NDB10AP010_-M01 |  | Motor | SGW REINJECTION PUMP A MOTOR (50%)
P020NDB10AP020_-M01 |  | Motor | SGW REINJECTION PUMP B MOTOR (50%)
P020NDB10AP030_-M01 |  | Motor | SGW REINJECTION PUMP C MOTOR (50%)
P020PCB20AP010_-M01 |  | Motor | SGW Pump VSD Cooling Circ Pump A Motor
P020PCB20AP020_-M01 |  | Motor | SGW Pump VSD Cooling Circ Pump B Motor
P020PCB20AP030_-M01 |  | Motor | SGW building sump pump motor
P020PCB31AH010_-M01 |  | Motor | Fin Fan Cooler A Motor 1
P020PCB31AH010_M02 |  | Motor | Fin Fan Cooler A Motor 2
P020PCB31AH010_M03 |  | Motor | Fin Fan Cooler A Motor 3
P020PCB31AH010_M04 |  | Motor | Fin Fan Cooler A Motor 4
P020PCB32AH020_-M01 |  | Motor | Fin Fan Cooler B Motor 1
P020PCB32AH020_M02 |  | Motor | Fin Fan Cooler B Motor 2
P020PCB32AH020_M03 |  | Motor | Fin Fan Cooler B Motor 3
P020PCB32AH020_M04 |  | Motor | Fin Fan Cooler B Motor 4
P020PCB33AH030_-M01 |  | Motor | Fin Fan Cooler C Motor 1
P020PCB33AH030_M02 |  | Motor | Fin Fan Cooler C Motor 2
P020PCB33AH030_M03 |  | Motor | Fin Fan Cooler C Motor 3
P020PCB33AH030_M04 |  | Motor | Fin Fan Cooler C Motor 4
P020QFA11AN001_-M01 |  | Motor | Air compressor motor
S020GAC20AP010_-M01 |  | Motor | Raw Water Pump A Motor
S020GAC20AP020_-M01 |  | Motor | Raw Water Pump B Motor
S020GBK10AP010_-M01 |  | Motor | Calcite inhibitor pump motor
S020GBK10AP020_-M01 |  | Motor | Calcite inhibitor bund sump pump motor
S020GKA10AP020_-M01 |  | Motor | Potable water pump B Motor
S020GKA20AP010_-M01 |  | Motor | Potable Water Pump A Motor
S020GKA20AP020_-M01 |  | Motor | Potable Water Pump B Motor
S020NDA21AH010_-M01 |  | Motor | Acid dilution cooler fan A Motor
S020NDA21AP010_-M01 |  | Motor | ACID DILUTION SGW PUMP (A) Motor
S020NDA21AP020_-M01 |  | Motor | Acid dilution cooler fan A Motor
S020NDA22AH020_-M01 |  | Motor | Acid dilution cooler fan B Motor
S020NDA22AP020_-M01 |  | Motor | ACID DILUTION SGW PUMP (B) Motor
S020QCM20AP010_-M01 |  | Motor | Acid Dosing Pump A Motor
S020QCM20AP020_-M01 |  | Motor | Acid dosing pump B Motor
S020QCM21AP020_-M01 |  | Motor | Acid Dosing Pump B Motor
S020QCM30AP001_-M01 |  | Motor | Acid dosing sump pump motor
S020QCM30AP001_-M01 |  | Motor | Acid dosing sump pump motor
P020NDB10AA110 |  | Motor operated valve | SGW PUMP A OUTLET MOV | ROTORK | IQ90 | Elecric actuator
P020NDB10AA120 |  | Motor operated valve | SGW PUMP B OUTLET MOV | ROTORK | IQ90 | Elecric actuator
P020NDB10AA130 |  | Motor operated valve | SGW PUMP C OUTLET MOV | ROTORK | IQ90 | Elecric actuator
P020NDB10AA140 |  | Motor operated valve | SGW PUMPS BYPASS MOV | ROTORK | TBA | Elecric actuator
L190NDB10AA001 |  | Motor operated valve | SGW CROSS COUNTRY LINE A ISOL MOV | ROTORK | TBA | Elecric actuator
L190NDB10AA002 |  | Motor operated valve | SGW CROSS COUNTRY LINE A MOV | ROTORK | IQ35 | Elecric actuator
L200NDB10AA001 |  | Motor operated valve | SGW CROSS COUNTRY LINE A MOV | ROTORK | IQ35 | Elecric actuator
L200NDB10AA002 |  | Motor operated valve | SGW CROSS COUNTRY LINE B MOV | ROTORK | IQ35 | Elecric actuator
P020NAB10AA030 |  | Motor operated valve | CONDENSATE PUMP A OUTLET MOV | ROTORK | TBA | Elecric actuator
P020NAB10AA110 |  | Motor operated valve | CONDENSATE PUMPS BYPASS MOV | ROTORK | IQ18 | Elecric actuator
P020LFC20AA010 |  | Motor operated valve | GFHP PUMP A OUTLET MOV | ROTORK | IQ18 | Elecric actuator
P020LFC20AA020 |  | Motor operated valve | GFHP PUMP B OUTLET MOV | ROTORK | IQ18 | Elecric actuator
S020NDB10AA053 |  | Motor operated valve | LP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB10AA054 |  | Motor operated valve | LP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB10AA013 |  | Motor operated valve | LP EDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB10AA023 |  | Motor operated valve | LP EDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB10AA033 |  | Motor operated valve | LP EDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA10AA043 |  | Motor operated valve | LP EDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA020 |  | Motor operated valve | LP SEPARATOR B OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB30AA021 |  | Motor operated valve | LP SEPARATOR B OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S060NDB10AA001 |  | Motor operated valve | LP SEPARATOR OUTLET MOV | ROTORK | IQ35 | Elecric actuator
L060NDA10AA030 |  | Motor operated valve | TH28 TO HP SEPARATOR MOV | ROTORK | IQ35 | Elecric actuator
L060NDA10AA040 |  | Motor operated valve | TH28 TO SILENCER MOV | ROTORK | IQ35 | Elecric actuator
L060NDA10AA050 |  | Motor operated valve | TH12 TO SILENCER MOV | ROTORK |  | Elecric actuator
L070NDA10AA030 |  | Motor operated valve | TH26 TO HP SEPARATOR MOV | ROTORK | IQ35 | Elecric actuator
L070NDA10AA040 |  | Motor operated valve | TH26 TO SILENCER MOV | ROTORK | IQ35 | Elecric actuator
L050NDA10AA030 |  | Motor operated valve | TH12 TO HP SEPARATOR MOV | ROTORK | IQ35 | Elecric actuator
L050NDA10AA040 |  | Motor operated valve | TH12 TO SILENCER MOV | ROTORK | IQ35 | Elecric actuator
S020NAA11AA110 |  | Motor operated valve | HP CDPS MOV | ROTORK | TBA | Elecric actuator
S020NAA10AA140 |  | Motor operated valve | HP SCRUBBER MOV | ROTORK | TBA | Elecric actuator
S020NAA31AA055 |  | Motor operated valve | LP STEAM SCRUBBING LINE A MOV | ROTORK | IQ40 | Elecric actuator
S020NAA31AA056 |  | Motor operated valve | LP STEAM SCRUBBING LINE A MOV | ROTORK | IQ40 | Elecric actuator
S020NAA32AA055 |  | Motor operated valve | LP STEAM SCRUBBING LINE B MOV | ROTORK | IQ40 | Elecric actuator
S020NAA32AA056 |  | Motor operated valve | LP STEAM SCRUBBING LINE B MOV | ROTORK | IQ40 | Elecric actuator
S020NAA10AA001 |  | Motor operated valve | HP STEAM SCRUBBING LINE MOV | ROTORK | IQ90 | Elecric actuator
S020NAA10AA002 |  | Motor operated valve | HP STEAM SCRUBBING LINE MOV | ROTORK | IQ90 | Elecric actuator
S020NAA20AA001 |  | Motor operated valve | IP STEAM SCRUBBING LINE MOV | ROTORK | IQ35 | Elecric actuator
S020NAA20AA002 |  | Motor operated valve | IP STEAM SCRUBBING LINE MOV | ROTORK | IQ35 | Elecric actuator
S020NAA31AA001 |  | Motor operated valve | LP STEAM SCRUBBING LINE A MOV | ROTORK | IQ90 | Elecric actuator
S020NAA31AA002 |  | Motor operated valve | LP STEAM SCRUBBING LINE A MOV | ROTORK | IQ90 | Elecric actuator
S020NAA32AA001 |  | Motor operated valve | LP STEAM SCRUBBING LINE B MOV | ROTORK | IQ90 | Elecric actuator
S020NAA32AA002 |  | Motor operated valve | LP STEAM SCRUBBING LINE B MOV | ROTORK | IQ90 | Elecric actuator
S020NDA20AA013 |  | Motor operated valve | HP LCV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA023 |  | Motor operated valve | HP LCV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA033 |  | Motor operated valve | HP LCV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA041 |  | Motor operated valve | HP EDV INLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA051 |  | Motor operated valve | HP EDV INLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA061 |  | Motor operated valve | HP EDV INLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA071 |  | Motor operated valve | HP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA072 |  | Motor operated valve | HP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA001 |  | Motor operated valve | HP SEPARATOR OUTLET MOV | ROTORK | IQ70 | Elecric actuator
S020NDA20AA002 |  | Motor operated valve | HP SEPARATOR OUTLET MOV | ROTORK | IQ70 | Elecric actuator
S020NDA20AA043 |  | Motor operated valve | HP EDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA20AA053 |  | Motor operated valve | HP EDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA20AA063 |  | Motor operated valve | HP EDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA20AA073 |  | Motor operated valve | HP MDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA20AA074 |  | Motor operated valve | HP MDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA30AA010 |  | Motor operated valve | LP SEPARATOR A OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA011 |  | Motor operated valve | LP SEPARATOR A OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA013 |  | Motor operated valve | IP LCV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA023 |  | Motor operated valve | IP LCV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA033 |  | Motor operated valve | IP LCV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA043 |  | Motor operated valve | IP LCV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA053 |  | Motor operated valve | IP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA054 |  | Motor operated valve | IP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA063 |  | Motor operated valve | IP EDV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA073 |  | Motor operated valve | IP EDV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA083 |  | Motor operated valve | IP EDV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA093 |  | Motor operated valve | IP EDV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA001 |  | Motor operated valve | IP SEPARATOR OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NAA31AA006 |  | Motor operated valve | LP SCRUBBING LINE BYPASS MOV | ROTORK | IQ40 | Elecric actuator
S020NAA31AA007 |  | Motor operated valve | LP SCRUBBING LINE BYPASS MOV | ROTORK | IQ40 | Elecric actuator
S020NDB10AA043 |  | Motor operated valve | LP EDV Outlet MOV | ROTORK |  | Elecric actuator
S020NDB10AA001 |  | Motor operated valve | LP Separator Outlet MOV | ROTORK |  | Elecric actuator
S020NDA30AA021 |  | Motor operated valve | LP Separator B Outlet MOV | ROTORK |  | Elecric actuator
S020GAC10AA021 |  | Motor operated valve | RAW WATER SYSTEM MOV | ROTORK |  | Elecric actuator
S020GAC10AA031 |  | Motor operated valve | RAW WATER SUPPLY MOV | ROTORK |  | Elecric actuator

## Circuit Breakers
Circuit Breaker Required Details
Note: The top row is the field description whereas the second line is the database descriptor.
Station | CB No. | Maintenance | System | Mtce Group | Assoc. Equip | Outage Period | General Notes | Vtge | Ser. No. | Plant | In/Out of service | Make | Rating | Model | Manual | KKS Code | Test Notes 1 | Test Notes 2 | Test Notes 3 | Test Notes 4 | Test Notes 5 | Test Notes 6 | Test Notes 7 | Test Notes 8 | Test Notes 9 | Test Notes 10 | Test Notes 11 | Test Notes 12 | Test Notes 13 | Test Notes 14
StationName | RelayName | Shutdown | SystemName | Mtce Group | Mtce Type | Outage Period | Notes | Fld1 | Fld2 | Fld3 | Fld4 | Fld5 | Fld6 | Fld7 | Fld8 | Fld9 | Fld10 | Fld11 | Fld12 | Fld13 | Fld14 | Fld15 | Fld16 | Fld17 | Fld18 | Fld19 | Fld20 | Fld21 | Fld22 | Fld23

## Cables
Cable Data Entry Sheet
NUMBER | RUN FROM | RUN TO | SIZE | CORES | SPARE | DRAWING | LENGTH | REMARKS | TYPE | INSTALLED
L050NDA10AA030 | L070NDA10AA040 TH26 to Silencer MOV | L050NDA10AA030 TH12 to HP Separator MOV | 22AWG | 1 Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
L050NDA10AA040 | L050NDA10AA030 TH12 to HP Separator MOV | L050NDA10AA040 TH12 to Silencer MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
L050NDA10CP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | L050NDA10CP010 TH12 Two Phase ISO Valve Pressure | 1.5mm2 | 2Pair |  | TAS2-205-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
L050NDA10CT010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | L050NDA10CT010 TH12 Two Phase ISO Valve Inlet Temperature | 1.5mm2 | 2Pair |  | TAS2-205-01 | 109.2 | C&I Sep | ESCS Cu - Tinned PVC / PVC
L060NDA10AA030 | S020NDB10AA001 LP Separator Outlet MOV | L060NDA10AA030 TH28 to HP Separator MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
L060NDA10AA040 | L060NDA10AA030 TH28 to HP Separator MOV | L060NDA10AA040 TH28 to Silencer MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
L060NDA10CP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | L060NDA10CP010 TH28 Two Phase ISO Valve Pressure | 1.5mm2 | 2Pair |  | TAS2-105-01 | 113.4 | C&I Sep | ESCS Cu - Tinned PVC / PVC
L060NDA10CT010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | L060NDA10CT010 TH28 Two Phase ISO Valve Inlet Temperature | 1.5mm2 | 2Pair |  | TAS2-105-01 | 118.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
L070NDA10AA030 | L060NDA10AA040 TH28 to Silencer MOV | L070NDA10AA030 TH26 to HP Separator MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
L070NDA10AA040 | L070NDA10AA030 TH26 to HP Separator MOV | L070NDA10AA040 TH26 to Silencer MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
L070NDA10CP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | L070NDA10CP010 TH26 Two Phase ISO Valve Pressure | 1.5mm2 | 2Pair |  | TAS2-105-01 | 113.4 | C&I Sep | ESCS Cu - Tinned PVC / PVC
L070NDA10CT010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | L070NDA10CT010 TH26 Two Phase ISO Valve Inlet Temperature | 1.5mm2 | 2Pair |  | TAS2-105-01 | 113.4 | C&I Sep | ESCS Cu - Tinned PVC / PVC
P020QFB10CP030 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | P020QFB10CP030 Instrument Air Pressure (BR0030) | 1.5mm2 | 2Pair |  | TAS2-206-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020BFA10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BFA10 Separation Plant LV Switchboard | 1.0mm2 | 24C+E |  | TAS2-505-01, TAS2-506-01, TAS2-506-02, TAS2-605-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BFA10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BFA10 Separation Plant LV Switchboard | 1.0mm2 | 24C+E |  | TAS2-412-02, TAS2-408-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BFA10GS00x0_Fab | S020BFA10HSW52 LV Switchboard - HSW52 | S020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - Acid Dilution SGW Pump A | 0.5mm2 | 4Pair |  | TAS2-805-02 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW52 LV Switchboard - HSW52 | S020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - Acid Dosing Sump Pump | 0.5mm2 | 4Pair |  | TAS2-805-02 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW52 LV Switchboard - HSW52 | S020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - General Lighting and Power A | 0.5mm2 | 4Pair |  | TAS2-805-02 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW52 LV Switchboard - HSW52 | S020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - Process DB A | 0.5mm2 | 4Pair |  | TAS2-805-02 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW52 LV Switchboard - HSW52 | S020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - HVAC System A | 0.5mm2 | 4Pair |  | TAS2-805-02 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW52 LV Switchboard - HSW52 | S020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - 110VDC System A | 0.5mm2 | 4Pair |  | TAS2-805-02 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW52 LV Switchboard - HSW52 | S020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - UPS System B Bypass | 0.5mm2 | 4Pair |  | TAS2-805-02 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW53 LV Switchboard - HSW53 | S020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - Acid Dilution SGW Pump B | 0.5mm2 | 4Pair |  | TAS2-805-03 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW53 LV Switchboard - HSW53 | S020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - General Lighting Bnd Power B | 0.5mm2 | 4Pair |  | TAS2-805-03 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW53 LV Switchboard - HSW53 | S020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - Process DB B | 0.5mm2 | 4Pair |  | TAS2-805-03 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW53 LV Switchboard - HSW53 | S020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - HVAC System B | 0.5mm2 | 4Pair |  | TAS2-805-03 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW53 LV Switchboard - HSW53 | S020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - 110VDC System B | 0.5mm2 | 4Pair |  | TAS2-805-03 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS00x0_Fab | S020BFA10HSW53 LV Switchboard - HSW53 | S020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - UPS System B Bypass | 0.5mm2 | 4Pair |  | TAS2-805-03 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS010_F02 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS010_F02 LV Switchboard Bus A - Bustie | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS010Q01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BFA10GS010Q01 Separation Plant LV Switchboard A - Bustie | 1.0mm2 | 12C+E |  | TAS2-505-01, TAS2-510-01, | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BFA10GS020_F02 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS020_F02 LV Switchboard Bus A - Incomer | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS020_F03 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS020_F03 LV Switchboard Bus A - Incomer Backup Protection | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS020_F03 | S020CRS20 Separation Plant Server Cabinet HSW7 | S020BFA10GS020_F03 LV Switchboard Bus A - Incomer Backup Protection Relay | 0.5mm2 | 4Pair |  | TAS2-804-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS020_F11 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS020_F11 LV Switchboard Bus A - Temp EDG Incomer | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS020_PQM1 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS020_PQM1 LV Switchboard Bus A - Power Meter | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS020_PQM2 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS020_PQM2 LV Switchboard Bus A - Temp Incomer PQM | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS020Q01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BFA10GS020Q01 Separation Plant LV Switchboard A - Incomer | 1.0mm2 | 12C+E |  | TAS2-505-01, TAS2-510-01, | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BFA10GS110_F02 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS110_F02 LV Switchboard Bus B - Bustie | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS110Q01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BFA10GS110Q01 Separation Plant LV Switchboard B - Bustie | 1.0mm2 | 12C+E |  | TAS2-605-01, TAS2-610-01, | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BFA10GS120_F02 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS120_F02 LV Switchboard Bus B - Incomer | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS120_F03 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS120_F03 LV Switchboard Bus B - Incomer Backup Protection | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS120_F03 | S020CRS20 Separation Plant Server Cabinet HSW8 | S020BFA10GS120_F03 LV Switchboard Bus B - Incomer Backup Protection Relay | 0.5mm2 | 4Pair |  | TAS2-804-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS120_F11 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS120_F11 LV Switchboard Bus B - Temp EDG Incomer | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS120_PQM1 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS120_PQM1 LV Switchboard Bus B - Power Meter | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS120_PQM2 | S020BFA10HSW51 LV Switchboard - HSW51 | S020BFA10GS120_PQM2 LV Switchboard Bus B - Temp Incomer PQM | 0.5mm2 | 4Pair |  | TAS2-805-04 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10GS120Q01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BFA10GS120Q01 Separation Plant LV Switchboard B - Incomer | 1.0mm2 | 12C+E |  | TAS2-605-01, TAS2-610-01, | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BFA10HSW51 | S020CRS20 Separation Plant Server Cabinet HSW5 | S020BFA10HSW51 LV Switchboard - HSW51 | 0.5mm2 | 4Pair |  | TAS2-805-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10HSW52 | S020CRS20 Separation Plant Server Cabinet HSW5 | S020BFA10HSW52 LV Switchboard - HSW52 | 0.5mm2 | 4Pair |  | TAS2-805-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10HSW53 | S020CRS20 Separation Plant Server Cabinet HSW5 | S020BFA10HSW53 LV Switchboard - HSW53 | 0.5mm2 | 4Pair |  | TAS2-805-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BFA10 | S020CRS20 Separation Plant Server Cabinet | S020BFA10 LV Switchboard IRIG-B | 1.5mm2 | 2Pair |  | TAS2-800-05 |  | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020BFT10GT010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BFT10GT010 Separation Plant Local Services Transformer 1 | 1.0mm2 | 12C+E |  | TAS2-505-02 | 71.4 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BFT10GT020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BFT10GT020 Separation Plant Local Services Transformer 2 | 1.0mm2 | 12C+E |  | TAS2-605-02 | 71.4 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BRA10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BRA10 230VAC Inverter A | 1.0mm2 | 12C+E |  | TAS2-508-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BRA10 | S020CRS20 Separation Plant Server Cabinet HSW5 | S020BRA10 230VAC Inverter A | 0.5mm2 | 4Pair |  | TAS2-805-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BRA10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BRA10 230VAC Inverter A | 1.0mm2 | 12Pair |  | TAS2-502-01 | 39.9 | C&I Sep | r ESCS Cu - Tinned PVC / PVC
S020BRB10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BRB10 230VAC Inverter B | 1.0mm2 | 12C+E |  | TAS2-608-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BRB10 | S020CRS20 Separation Plant Server Cabinet HSW5 | S020BRB10 230VAC Inverter B | 0.5mm2 | 4Pair |  | TAS2-805-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BRB10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BRB10 230VAC Inverter B | 1.0mm2 | 12Pair |  | TAS2-602-01 | 39.9 | C&I Sep | r ESCS Cu - Tinned PVC / PVC
S020BTL10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BTL10 110VDC Power Supply System A | 1.0mm2 | 12C+E |  | TAS2-508-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BTL10 | S020CRS20 Separation Plant Server Cabinet HSW5 | S020BTL10 110VDC System A | 0.5mm2 | 4Pair |  | TAS2-805-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BTL10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BTL10 110VDC Power Supply System A | 1.0mm2 | 12Pair |  | TAS2-502-01 | 39.9 | C&I Sep | r ESCS Cu - Tinned PVC / PVC
S020BTM10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BTM10 110VDC Power Supply System B | 1.0mm2 | 12C+E |  | TAS2-608-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020BTM10 | S020CRS20 Separation Plant Server Cabinet HSW5 | S020BTM10 110VDC System B | 0.5mm2 | 4Pair |  | TAS2-805-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020BTM10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020BTM10 110VDC Power Supply System B | 1.0mm2 | 12Pair |  | TAS2-602-01 | 39.9 | C&I Sep | r ESCS Cu - Tinned PVC / PVC
S020CRA20 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CRA20 Steamfield PLC Cabinet - TAS1 | 1.0mm2 | 24C+E |  | TAS2-504-01, TAS2-506-01 | 21 | C&I Sep | CS Cu - Tinned PVC / PVC
S020CRA20 | S020CRS20 Separation Plant Server Cabinet | S020CRA20 Separation Plant PLC Cabinet - TAS1 CPU 1 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRA20 | S020CRS20 Separation Plant Server Cabinet | S020CRA20 Separation Plant PLC Cabinet - TAS1 CPU 1 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRA20 | S020CRS20 Separation Plant Server Cabinet | S020CRA20 Separation Plant PLC Cabinet - TAS1 CPU 2 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRA20 | S020CRS20 Separation Plant Server Cabinet | S020CRA20 Separation Plant PLC Cabinet - TAS1 CPU 2 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRA20 | S020CRS20 Separation Plant Server Cabinet HSW21 | S020CRA20 Separation Plant PLC Cabinet - TAS1 | 22AWG | 1Pair |  | TAS1-803-01 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020CRA20 | S020CRS20 Separation Plant Server Cabinet HSW22 | S020CRA20 Separation Plant PLC Cabinet - TAS1 | 22AWG | 1Pair |  | TAS1-803-02 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020CRA20 | S020CRS20 Separation Plant Server Cabinet HSW23 | S020CRA20 Separation Plant PLC Cabinet - TAS1 | 22AWG | 1Pair |  | TAS1-803-03 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020CRA20 | S020CRS20 Separation Plant Server Cabinet HSW24 | S020CRA20 Separation Plant PLC Cabinet - TAS1 | 22AWG | 1Pair |  | TAS1-803-04 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020CRA20 | S020CRS20 Separation Plant Server Cabinet HSW25 | S020CRA20 Separation Plant PLC Cabinet - TAS1 | 22AWG | 1Pair |  | TAS1-803-05 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020CRA20 | S020CRS20 Separation Plant Server Cabinet HSW26 | S020CRA20 Separation Plant PLC Cabinet - TAS1 | 22AWG | 1Pair |  | TAS1-803-06 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020CRA20 | S020CRS20 Separation Plant Server Cabinet HSW27 | S020CRA20 Separation Plant PLC Cabinet - TAS1 | 22AWG | 1Pair |  | TAS1-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020CRA20 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CRA20 Steamfield PLC Cabinet - TAS1 | 1.0mm2 | 4Pair |  | TAS2-501-01 | 21 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020CRA30 | - Tauhara Power Plant | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 2 | 1.5mm2 | 19C |  | TASs-412-02 | 769.65 | C&I Sep | #NAME?
S020CRA30 | - Tauhara Power Plant | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 2 | 1.5mm2 | 12Pair |  | TAS2-310-02, TAS2-410-02 | 769.65 | C&I Sep | r CS Cu - Tinned PVC / PVC
S020CRA30 | S020CRS20 Separation Plant Server Cabinet | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 1 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRA30 | S020CRS20 Separation Plant Server Cabinet | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 1 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRA30 | S020CRS20 Separation Plant Server Cabinet | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 2 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRA30 | S020CRS20 Separation Plant Server Cabinet | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 2 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRA30 | - Tauhara Power Plant | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 2 | 1.5mm2 | 12Pair |  | TAS2-405-01, TAS2-307-01, TAS2-402-01 | 769.65 | C&I Sep | r ESCS Cu - Tinned PVC / PVC
S020CRJ40 | S020CRS20 Separation Plant Server Cabinet | S020CRJ40 Separation Plant PLC Cabinet - TAS4 CPU 1 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRJ40 | S020CRS20 Separation Plant Server Cabinet | S020CRJ40 Separation Plant PLC Cabinet - TAS4 CPU 1 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRJ40 | S020CRS20 Separation Plant Server Cabinet | S020CRJ40 Separation Plant PLC Cabinet - TAS4 CPU 2 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRJ40 | S020CRS20 Separation Plant Server Cabinet | S020CRJ40 Separation Plant PLC Cabinet - TAS4 CPU 2 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CRS20 Server Cabinet NSP | 1.0mm2 | 24C+E |  | TAS2-604-01, TAS2-506-01 | 21 | C&I Sep | CS Cu - Tinned PVC / PVC
S020CRS20HSW5 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CRS20HSW5 Separation Plant Server Cabinet HSW5 | 0.5mm2 | 4Pair |  | TAS2-805-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRS20 | - Tauhara Power Plant | S020CRS20 Separation Plant Server Cabinet NSP | 9/125μm | 96Core |  | (*)CCI-SDG-1805 | 769.65 | C&I Sep | re Singlemode OS2 PE Outdoor Jacket
S020CRS20 | P020CRS10 Pump Station Server Cabinet NSP | S020CRS20 Separation Plant Server Cabinet NSP | 9/125μm | 48Core |  | (*)CCI-SDG-1805 | 543.9 | C&I Sep | re Singlemode OS2 PE Outdoor Jacket
S020CRS20 | P020CRS10 Pump Station Server Cabinet NSP | S020CRS20 Separation Plant Server Cabinet NSP | 9/125μm | 48Core |  | (*)CCI-SDG-1805 | 606.9 | C&I Sep | re Singlemode OS2 PE Outdoor Jacket
S020CRS20 | - Unison 33/11kV Tauhara Substation | S020CRS20 Separation Plant Server Cabinet NSP | 9/125μm | 48Core |  | (*)CCI-SDG-1805 | 249.9 | C&I Sep | re Singlemode OS2 PE Outdoor Jacket
S020CRS20 | - Unison 33/11kV Tauhara Substation | S020CRS20 Separation Plant Server Cabinet NSP | 9/125μm | 48Core |  | (*)CCI-SDG-1805 | 207.9 | C&I Sep | re Singlemode OS2 PE Outdoor Jacket
S020CRS20 | - Unison 33/11kV Tauhara Substation | S020CRS20 Separation Plant Server Cabinet NSP | 50/125μm | 12Core |  | (*)CCI-SDG-1805 | 228.9 | C&I Sep | ore Multimode OM3 PE Outdoor Jacket
S020CRS20 | P020CRS10 Pump Station Server Cabinet NSP | S020CRS20 Separation Plant Server Cabinet NSP | 50/125μm | 24Core |  | (*)CCI-SDG-1805 | 543.9 | C&I Sep | ore Multimode OM3 PE Outdoor Jacket
S020CRS20 | S020CRS20 Separation Plant Server Cabinet - Tekron Clock | S020CRS20 Separation Plant Server Cabinet - MC11 | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRS20 Separation Plant Server Cabinet - HSW1 | S020CRS20 Separation Plant Server Cabinet - Tekron Clock | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRS20 Separation Plant Server Cabinet - HSW2 | S020CRS20 Separation Plant Server Cabinet - Tekron Clock | 0.5mm2 | 4Pair |  | TAS2-802-01 | 21 | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRS20 Separation Plant Server Cabinet | S020CRS20 Separation Plant Server Cabinet - VM Host 1 | 0.5mm2 | 4Pair |  | TAS2-802-01 |  | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRS20 Separation Plant Server Cabinet | S020CRS20 Separation Plant Server Cabinet - VM Host 1 | 0.5mm2 | 4Pair |  | TAS2-802-01 |  | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRS20 Separation Plant Server Cabinet | S020CRS20 Separation Plant Server Cabinet - VM Host 1 | 0.5mm2 | 4Pair |  | TAS2-802-02 |  | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRS20 Separation Plant Server Cabinet | S020CRS20 Separation Plant Server Cabinet - VM Host 1 | 0.5mm2 | 4Pair |  | TAS2-802-02 |  | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRS20 Separation Plant Server Cabinet | S020CRS20 Separation Plant Server Cabinet - VM Host 1 | 0.5mm2 | 4Pair |  | TAS2-804-01 |  | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRS20 Separation Plant Server Cabinet | S020CRS20 Separation Plant Server Cabinet - VM Host 1 | 0.5mm2 | 4Pair |  | TAS2-808-02 |  | C&I Sep | Cu - CAT6 STP
S020CRS20 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CRS20 Server Cabinet NSP | 1.0mm2 | 4Pair |  | TAS2-601-01 | 21 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020CRS40 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CRS40 Server Cabinet Building Services | 1.0mm2 | 12C+E |  | , TAS2-507-01, TAS2-604-02 | 21 | C&I Sep | CS Cu - Tinned PVC / PVC
S020CRS40 | S020CRS20 Separation Plant Server Cabinet NSP | S020CRS40 Separation Plant Server Cabinet Building Services | 9/125μm | 24Core |  | (*)CCI-SDG-1805 | 15 | C&I Sep | re Singlemode OS2
S020CRS40 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CRS40 Server Cabinet Building Services | 1.0mm2 | 4Pair |  | TAS2-601-01 | 21 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020CRU10 | S020CRS20 Separation Plant Server Cabinet | S020CRU10 OWS | 0.5mm2 | 4Pair |  | TAS2-802-02 | 39.9 | C&I Sep | Cu - CAT6 STP
S020CRU10 | S020CRS20 Separation Plant Server Cabinet | S020CRU10 OWS | 0.5mm2 | 4Pair |  | TAS2-802-02 | 39.9 | C&I Sep | Cu - CAT6 STP
S020CVA41 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CVA41 Separation Plant RTD Junction Box | 1.0mm2 | 12Triple |  | - | 129.15 | C&I Sep | ple ESCS Cu - Tinned PVC / PVC
S020CVA42 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CVA42 Separation Plant RTD Junction Box | 1.0mm2 | 12Triple |  | - | 134.4 | C&I Sep | ple ESCS Cu - Tinned PVC / PVC
S020CVA43 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CVA43 Separation Plant RTD Junction Box | 1.0mm2 | 12Triple |  | - | 144.9 | C&I Sep | ple ESCS Cu - Tinned PVC / PVC
S020CVA44 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CVA44 Separation Plant RTD Junction Box | 1.0mm2 | 12Triple |  | - | 178.5 | C&I Sep | ple ESCS Cu - Tinned PVC / PVC
S020CVA45 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020CVA45 Separation Plant RTD Junction Box | 1.0mm2 | 12Triple |  | - | 162.75 | C&I Sep | ple ESCS Cu - Tinned PVC / PVC
S020GAC10AA021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC10AA021 Raw Water Supply Motorised Valve | 1.0mm2 | 12C+E |  | TAS2-309-02, TAS2-311-02 | 102.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020GAC10AA031 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC10AA031 Raw Water Supply Motorised Valve | 1.0mm2 | 12C+E |  | TAS2-409-02, TAS2-411-02 | 102.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020GAC10CL010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC10CL010 Raw Water Tank 1 Level Indicator | 1.5mm2 | 2Pair |  | TAS2-111-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GAC10CL010 | S020GAC10CL010 Raw Water Tank 1 Level Indicator | S020GAC10CL010 Raw Water Tank 1 Level | 1.5mm2 | 2Pair |  | TAS2-111-01 | 12 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GAC10CL011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC10CL011 Raw Water Tank 2 Level Indicator | 1.5mm2 | 2Pair |  | TAS2-211-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GAC10CL011 | S020GAC10CL011 Raw Water Tank 2 Level Indicator | S020GAC10CL011 Raw Water Tank 2 Level | 1.5mm2 | 2Pair |  | TAS2-211-01 | 12 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GAC10CP001 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC10CP001 Raw Water Supply Diff Pressure | 1.5mm2 | 2Pair |  | TAS2-211-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GAC10CP002 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC10CP002 Raw Water Supply Pressure | 1.5mm2 | 2Pair |  | TAS2-211-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GAC20AP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC20AP010 Raw Water Pump A | 1.0mm2 | 12C+E |  | TAS2-508-02, TAS2-510-02 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020GAC20AP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC20AP010 Raw Water Pump A | 1.5mm2 | 2Pair |  | TAS2-503-01 | 39.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GAC20AP020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC20AP020 Raw Water Pump B | 1.0mm2 | 12C+E |  | TAS2-608-02, | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020GAC20AP020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC20AP020 Raw Water Pump B | 1.5mm2 | 2Pair |  | TAS2-603-01 | 39.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GAC21CP020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GAC21CP020 Raw Water Pump Station Out Pressure | 1.5mm2 | 2Pair |  | TAS2-111-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GBK10AP010 (S020BFA10) | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GBK10AP010 (S020BFA10) Calcite Inhibitor Pump MCC Cell | 1.0mm2 | 12C+E |  | TAS2-410-01, TAS2-412-02 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020GBK10AP020 (S020BFA10) | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GBK10AP020 (S020BFA10) Calcite Inhibitor Bund Sump Pump MCC Cell | 1.0mm2 | 12C+E |  | TAS2-410-01, TAS2-412-02 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020GBK10CL010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GBK10CL010 Calcite Inhibitor Tank Level | 1.5mm2 | 2Pair |  | TAS2-106-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GBK10CL010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GBK10CL010 Calcite Inhibitor Tank Level | 1.5mm2 | 2Pair |  | TAS2-106-01 | 12 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GBK10CL011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GBK10CL011 Calcite Inhibitor Dosing System Bund Level Indicator | 1.5mm2 | 2Pair |  | TAS2-106-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GBK10CL011 | S020CRA30 Calcite Inhibitor Dosing System Bund Level Indicator | S020GBK10CL011 Calcite Inhibitor Dosing System Bund Level | 1.5mm2 | 2Pair |  | TAS2-106-01 | 12 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GBK11CL012 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GBK11CL012 Calcite Inhibitor Dosing System Bund Level Indicator | 1.5mm2 | 2Pair |  | TAS2-206-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GBK11CL012 | S020CRA30 Calcite Inhibitor Dosing System Bund Level Indicator | S020GBK11CL012 Calcite Inhibitor Dosing System Bund Level | 1.5mm2 | 2Pair |  | TAS2-206-01 | 12 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GKA10CL010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA10CL010 Potable Water Tank 1 Level Indicator | 1.5mm2 | 2Pair |  | TAS2-111-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GKA10CL010 | S020GKA10CL010 Potable Water Tank 1 Level Indicator | S020GKA10CL010 Potable Water Tank 1 Level | 1.5mm2 | 2Pair |  | TAS2-111-01 | 12 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GKA10CL011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA10CL011 Potable Water Tank 2 Level Indicator | 1.5mm2 | 2Pair |  | TAS2-211-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GKA10CL011 | S020GKA10CL011 Potable Water Tank 2 Level Indicator | S020GKA10CL011 Potable Water Tank 2 Level | 1.5mm2 | 2Pair |  | TAS2-211-01 | 12 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GKA20AP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA20AP010 Potable Water Supply A Package | 1.0mm2 | 12C+E |  | TAS2-508-02, TAS2-510-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020GKA20AP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA20AP010 Potable Water Supply A Package | 1.5mm2 | 2Pair |  | TAS2-503-01 | 39.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GKA20AP020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA20AP020 Potable Water Supply B Package | 1.0mm2 | 12C+E |  | TAS2-608-02, TAS2-610-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020GKA20AP020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA20AP020 Potable Water Supply B Package | 1.5mm2 | 2Pair |  | TAS2-603-01, TAS2-610-02 | 39.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GKA21CF191 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA21CF191 Acid Dosing Emergency Eye Wash Flow | 1.5mm2 | 1Triple |  | TAS2-112-01 | 144.9 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020GKA21CF192 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA21CF192 Acid Dosing Emergency Eye Wash Flow | 1.5mm2 | 1Triple |  | TAS2-112-01 | 144.9 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020GKA21CF193 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA21CF193 Acid Dosing Emergency Eye Wash Flow | 1.5mm2 | 1Triple |  | TAS2-212-01 | 159.6 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020GKA21CF194 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA21CF194 SP Battery Room Eye Wash Flow | 1.5mm2 | 1Triple |  | TAS2-212-01 | 39.9 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020GKA21CP520 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA21CP520 Potable Water Pump Station Out Pressure | 1.5mm2 | 2Pair |  | TAS2-111-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020GKA22AA002_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA002_Y01 HP SGW Sampling Potable Water ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-510-01 | 123.9 | C&I Sep | u - Tinned PVC / PVC
S020GKA22AA002 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA002 HP SGW Sampling Potable Water ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-112-02 | 123.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020GKA22AA012_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA012_Y01 HP SGW Sampling Potable Water ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-212-02 | 123.9 | C&I Sep | u - Tinned PVC / PVC
S020GKA22AA012 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA012 HP SGW Sampling Potable Water ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-610-01 | 123.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020GKA22AA022_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA022_Y01 LP SGW Sampling Potable Water ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-510-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020GKA22AA022 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA022 LP SGW Sampling Potable Water ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-506-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020GKA22AA032_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA032_Y01 LP SGW Sampling Potable Water ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-610-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020GKA22AA032 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA032 LP SGW Sampling Potable Water ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-604-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020GKA22AA042_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA042_Y01 LP SGW Sampling Potable Water ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-610-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020GKA22AA042 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA042 LP SGW Sampling Potable Water ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-604-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020GKA22AA052_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA052_Y01 LP SGW Sampling Potable Water ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-510-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020GKA22AA052 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020GKA22AA052 LP SGW Sampling Potable Water ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-507-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020LCE10AA110 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE10AA110 HP Steam Scrubbing Wash Water FCV | 1.0mm2 | 4Pair |  | TAS2-301-01, TAS2-306-01 | 265.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE10AA120 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE10AA120 IP Steam Scrubbing Wash Water FCV | 1.0mm2 | 4Pair |  | TAS2-301-01, TAS2-306-01 | 265.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE10AA130 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE10AA130 LP Steam Scrubbing A Wash Water FCV | 1.0mm2 | 4Pair |  | TAS2-401-01 | 265.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE10AA140 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE10AA140 LP Steam Scrubbing B Wash Water FCV | 1.0mm2 | 4Pair |  | TAS2-401-01, TAS2-406-01 | 265.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE10CF010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE10CF010 HP Steam Scrubbing Wash Water FCV Flow | 1.5mm2 | 2Pair |  | TAS2-109-01 | 265.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE10CF020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE10CF020 IP Steam Scrubbing Wash Water FCV Flow | 1.5mm2 | 2Pair |  | TAS2-209-01 | 265.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE10CF030 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE10CF030 LP Steam Scrubbing A Wash Water FCV Flow | 1.5mm2 | 2Pair |  | TAS2-109-01 | 265.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE10CF040 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE10CF040 LP Steam Scrubbing B Wash Water FCV Flow | 1.5mm2 | 2Pair |  | TAS2-209-01 | 265.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE20CL010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE20CL010 Deoxygenated Process Water Tank 1 Level | 1.5mm2 | 2Pair |  | TAS2-106-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE20CL010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE20CL010 Deoxygenated Process Water Tank 1 Level | 1.5mm2 | 2Pair |  | TAS2-106-01 | 12 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE20CL011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE20CL011 Deoxygenated Process Water Tank 2 Level | 1.5mm2 | 2Pair |  | TAS2-206-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LCE20CL011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020LCE20CL011 Deoxygenated Process Water Tank 2 Level | 1.5mm2 | 2Pair |  | TAS2-206-01 | 12 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020LFC10CT001 | S020CVA45 Separation Plant RTD Junction Box | S020LFC10CT001 TH12 Two Phase Rupture Discs Temperature | 1.5mm2 | 1Triple |  | TAS2-201-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT002 | S020CVA45 Separation Plant RTD Junction Box | S020LFC10CT002 TH12 Two Phase Rupture Discs Temperature | 1.5mm2 | 1Triple |  | TAS2-203-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT003 | S020CVA45 Separation Plant RTD Junction Box | S020LFC10CT003 TH12 Two Phase Rupture Discs Temperature | 1.5mm2 | 1Triple |  | TAS2-201-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT011 | S020CVA45 Separation Plant RTD Junction Box | S020LFC10CT011 TH28 Two Phase Rupture Discs Temperature | 1.5mm2 | 1Triple |  | TAS2-101-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT012 | S020CVA45 Separation Plant RTD Junction Box | S020LFC10CT012 TH28 Two Phase Rupture Discs Temperature | 1.5mm2 | 1Triple |  | TAS2-103-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT013 | S020CVA45 Separation Plant RTD Junction Box | S020LFC10CT013 TH28 Two Phase Rupture Discs Temperature | 1.5mm2 | 1Triple |  | TAS2-104-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT021 | S020CVA45 Separation Plant RTD Junction Box | S020LFC10CT021 TH26 Two Phase Rupture Discs Temperature | 1.5mm2 | 1Triple |  | TAS2-101-01 | 27 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT022 | S020CVA45 Separation Plant RTD Junction Box | S020LFC10CT022 TH26 Two Phase Rupture Discs Temperature | 1.5mm2 | 1Triple |  | TAS2-103-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT023 | S020CVA45 Separation Plant RTD Junction Box | S020LFC10CT023 TH26 Two Phase Rupture Discs Temperature | 1.5mm2 | 1Triple |  | TAS2-104-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT041 | S020CVA41 Separation Plant RTD Junction Box | S020LFC10CT041 HP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-101-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT042 | S020CVA41 Separation Plant RTD Junction Box | S020LFC10CT042 HP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-102-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT043 | S020CVA41 Separation Plant RTD Junction Box | S020LFC10CT043 HP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-103-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT044 | S020CVA41 Separation Plant RTD Junction Box | S020LFC10CT044 HP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-201-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT045 | S020CVA41 Separation Plant RTD Junction Box | S020LFC10CT045 HP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-202-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT046 | S020CVA41 Separation Plant RTD Junction Box | S020LFC10CT046 HP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-203-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT051 | S020CVA42 Separation Plant RTD Junction Box | S020LFC10CT051 IP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-101-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT052 | S020CVA42 Separation Plant RTD Junction Box | S020LFC10CT052 IP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-102-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT053 | S020CVA42 Separation Plant RTD Junction Box | S020LFC10CT053 IP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-103-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT054 | S020CVA42 Separation Plant RTD Junction Box | S020LFC10CT054 IP Steam Scrubbing Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-201-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT061 | S020CVA43 Separation Plant RTD Junction Box | S020LFC10CT061 LP Steam Scrubbing A Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-201-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT062 | S020CVA43 Separation Plant RTD Junction Box | S020LFC10CT062 LP Steam Scrubbing A Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-102-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT063 | S020CVA43 Separation Plant RTD Junction Box | S020LFC10CT063 LP Steam Scrubbing A Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-103-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT064 | S020CVA43 Separation Plant RTD Junction Box | S020LFC10CT064 LP Steam Scrubbing A Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-201-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT065 | S020CVA43 Separation Plant RTD Junction Box | S020LFC10CT065 LP Steam Scrubbing A Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-202-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT066 | S020CVA43 Separation Plant RTD Junction Box | S020LFC10CT066 LP Steam Scrubbing A Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-203-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT071 | S020CVA44 Separation Plant RTD Junction Box | S020LFC10CT071 LP Steam Scrubbing B Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-101-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT072 | S020CVA44 Separation Plant RTD Junction Box | S020LFC10CT072 LP Steam Scrubbing B Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-102-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT073 | S020CVA44 Separation Plant RTD Junction Box | S020LFC10CT073 LP Steam Scrubbing B Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-103-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT074 | S020CVA44 Separation Plant RTD Junction Box | S020LFC10CT074 LP Steam Scrubbing B Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-201-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT075 | S020CVA44 Separation Plant RTD Junction Box | S020LFC10CT075 LP Steam Scrubbing B Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-202-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020LFC10CT076 | S020CVA44 Separation Plant RTD Junction Box | S020LFC10CT076 LP Steam Scrubbing B Rupture Disc Temperature | 1.5mm2 | 1Triple |  | TAS2-203-01 | 26.25 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020NAA10AA001 | S020NAA32AA056 LP Steam Scrubbing Line B MOV | S020NAA10AA001 HP Steam Scrubbing Line MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA10AA002 | S020NAA10AA001 HP Steam Scrubbing Line MOV | S020NAA10AA002 HP Steam Scrubbing Line MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA10AA101 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA10AA101 HP Steam Scrubbing LCV | 1.0mm2 | 4Pair |  | TAS2-301-01, TAS2-306-01 | 404.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA10AA140 | S020NAA11AA110 HP CDPS MOV | S020NAA10AA140 HP SCRUBBER MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA10CF010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA10CF010 HP Steam Scrubbing Flow | 1.5mm2 | 2Pair |  | TAS2-209-01 | 265.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA10CF452 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA10CF452 HP Steam Scrubbing Flow | 1.5mm2 | 2Pair |  | TAS2-109-01 | 404.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA10CL451 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA10CL451 Steam Trap Bank (HP Steam Scrubbing) Level | 1.5mm2 | 2Pair |  | TAS2-109-01 | 404.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA10CP021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA10CP021 HP Separator Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-106-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA10CP022 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA10CP022 HP Separator Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-107-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA10CP023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA10CP023 HP Separator Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-206-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA11AA110 | L050NDA10AA040 TH12 to Silencer MOV | S020NAA11AA110 HP CDPS MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA20AA001 | S020NAA10AA002 HP Steam Scrubbing Line MOV | S020NAA20AA001 IP Steam Scrubbing Line MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA20AA002 | S020NAA20AA001 IP Steam Scrubbing Line MOV | S020NAA20AA002 IP Steam Scrubbing Line MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA20CF010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA20CF010 IP Steam Scrubbing Flow | 1.5mm2 | 2Pair |  | TAS2-209-01 | 391.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA20CP021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA20CP021 IP Separator Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-106-01 | 108.15 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA20CP022 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA20CP022 IP Separator Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-107-01 | 108.15 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA20CP023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA20CP023 IP Separator Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-207-01 | 108.15 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA31AA001 | S020NAA20AA002 IP Steam Scrubbing Line MOV | S020NAA31AA001 LP Steam Scrubbing Line A MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA31AA002 | S020NAA31AA001 LP Steam Scrubbing Line A MOV | S020NAA31AA002 LP Steam Scrubbing Line A MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA31AA006 | S020NDA30AA001 IP Separator Outlet MOV | S020NAA31AA006 LP Scrubbing Line Bypass MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA31AA007 | S020NAA31AA006 LP Scrubbing Line Bypass MOV | S020NAA31AA007 LP Scrubbing Line Bypass MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA31AA055 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA31AA055 LP Steam Scrubbing Line A MOV | 22AWG | 1Pair |  | TAS2-803-08 | 144.9 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA31AA056 | S020NAA31AA055 LP Steam Scrubbing Line A MOV | S020NAA31AA056 LP Steam Scrubbing Line A MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA31CF010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA31CF010 LP Steam Scrubbing A Flow | 1.5mm2 | 2Pair |  | TAS2-109-01 | 391.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA31CP021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA31CP021 LP Separator A Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-108-01 | 58.8 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA31CP022 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA31CP022 LP Separator A Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-109-01 | 58.8 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA31CP023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA31CP023 LP Separator A Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-208-01 | 58.8 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA32AA001 | S020NAA31AA002 LP Steam Scrubbing Line A MOV | S020NAA32AA001 LP Steam Scrubbing Line B MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA32AA002 | S020NAA32AA001 LP Steam Scrubbing Line B MOV | S020NAA32AA002 LP Steam Scrubbing Line B MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA32AA055 | S020NAA31AA056 LP Steam Scrubbing Line A MOV | S020NAA32AA055 LP Steam Scrubbing Line B MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA32AA056 | S020NAA32AA055 LP Steam Scrubbing Line B MOV | S020NAA32AA056 LP Steam Scrubbing Line B MOV | 22AWG | 1Pair |  | TAS2-803-08 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NAA32CF010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA32CF010 LP Steam Scrubbing B Flow | 1.5mm2 | 2Pair |  | TAS2-209-01 | 391.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA32CP021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA32CP021 LP Separator B Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-108-01 | 90.3 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA32CP022 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA32CP022 LP Separator B Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-209-01 | 89.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA32CP023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NAA32CP023 LP Separator B Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-108-01 | 89.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA10CL021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA10CL021 HP SGW Drum Level | 1.5mm2 | 2Pair |  | TAS2-106-01 | 186.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA10CL022 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA10CL022 HP SGW Drum Level | 1.5mm2 | 2Pair |  | TAS2-107-01 | 186.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA10CL023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA10CL023 HP SGW Drum Level | 1.5mm2 | 2Pair |  | TAS2-206-01 | 186.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA10CP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA10CP010 HP Separator Inlet Pressure | 1.5mm2 | 2Pair |  | TAS2-106-01 | 134.4 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA10CT010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA10CT010 TH12 Two Phase ISO Valve Outlet Temperature | 1.5mm2 | 2Pair |  | TAS2-205-01 | 121.8 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA10CT020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA10CT020 TH28 Two Phase ISO Valve Outlet Temperature | 1.5mm2 | 2Pair |  | TAS2-105-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA10CT030 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA10CT030 TH26 Two Phase ISO Valve Outlet Temperature | 1.5mm2 | 2Pair |  | TAS2-105-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20AA001 | S020NDA20AA072 HP MDV Inlet MOV | S020NDA20AA001 HP Separator Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA002 | S020NDA20AA001 HP Separator Outlet MOV | S020NDA20AA002 HP Separator Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA013 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA013 HP LCV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 144.9 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA023 | S020NDA20AA013 HP LCV Outlet MOV | S020NDA20AA023 HP LCV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA033 | S020NDA20AA023 HP LCV Outlet MOV | S020NDA20AA033 HP LCV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA041 | S020NDA20AA033 HP LCV Outlet MOV | S020NDA20AA041 HP EDV Inlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA043 | S020NDA20AA002 HP Separator Outlet MOV | S020NDA20AA043 HP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA051 | S020NDA20AA041 HP EDV Inlet MOV | S020NDA20AA051 HP EDV Inlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA053 | S020NDA20AA043 HP EDV Outlet MOV | S020NDA20AA053 HP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA061 | S020NDA20AA051 HP EDV Inlet MOV | S020NDA20AA061 HP EDV Inlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA063 | S020NDA20AA053 HP EDV Outlet MOV | S020NDA20AA063 HP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA071 | S020NDA20AA061 HP EDV Inlet MOV | S020NDA20AA071 HP MDV Inlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA072 | S020NDA20AA071 HP MDV Inlet MOV | S020NDA20AA072 HP MDV Inlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA073 | S020NDA20AA063 HP EDV Outlet MOV | S020NDA20AA073 HP MDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA074 | S020NDA20AA073 HP MDV Outlet MOV | S020NDA20AA074 HP MDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-12 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA20AA110 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA110 HP Level Control Valve - LCV Position Switches | 1.0mm2 | 7C+E |  | TAS2-310-01 | 136.5 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA20AA110 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA110 HP Level Control Valve - LCV Position | 1.0mm2 | 4Pair |  | TAS2-301-01, TAS2-306-01 | 136.5 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20AA120 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA120 HP Level Control Valve - LCV Position Switches | 1.0mm2 | 7C+E |  | TAS2-310-02 | 136.5 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA20AA120 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA120 HP Level Control Valve - LCV Position | 1.0mm2 | 4Pair |  | TAS2-302-01, TAS2-307-01 | 136.5 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20AA130 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA130 HP Level Control Valve - LCV Position Switches | 1.0mm2 | 7C+E |  | TAS2-410-02 | 136.5 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA20AA130 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA130 HP Level Control Valve - LCV Position | 1.0mm2 | 4Pair |  | TAS2-401-01, TAS2-406-01 | 136.5 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20AA140 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA140 HP Emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-303-01 | 181.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20AA150 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA150 HP Emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-303-01 | 181.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20AA160 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA160 HP Emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-403-01 | 181.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20AA170 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA170 HP Modulating Dump Valve - MDV Solenoid | 2.5mm2 | 2C+E |  | TAS2-312-01 | 157.5 | C&I Sep | u - Tinned PVC / PVC
S020NDA20AA170 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA170 HP Modulating Dump Valve - MDV Position Switches | 1.0mm2 | 7C+E |  | TAS2-310-02 | 157.5 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA20AA170 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20AA170 HP Modulating Dump Valve - MDV Position | 1.0mm2 | 4Pair |  | TAS2-301-01,TAS2-306-01 | 157.5 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20CF010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20CF010 HP SGW Drum Outlet Flow | 1.5mm2 | 2Pair |  | TAS2-206-01 | 127.05 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20CF020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20CF020 HP SGW Drum Outlet Flow | 1.5mm2 | 2Pair |  | TAS2-302-01 | 127.05 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20CL021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20CL021 IP SGW Drum Level | 1.5mm2 | 2Pair |  | TAS2-106-01 | 113.4 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20CL022 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20CL022 IP SGW Drum Level | 1.5mm2 | 2Pair |  | TAS2-107-01 | 113.4 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20CL023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20CL023 IP SGW Drum Level | 1.5mm2 | 2Pair |  | TAS2-207-01 | 113.4 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA20CP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA20CP010 IP Separator Inlet Pressure | 1.5mm2 | 2Pair |  | TAS2-107-01 | 94.5 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA21AA013_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21AA013_Y01 Acid Dilution SGW Pump A Control Valve Solenoid | 2.5mm2 | 2C+E |  | TAS2-312-01 | 159.6 | C&I Sep | u - Tinned PVC / PVC
S020NDA21AA013 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21AA013 Acid Dilution SGW Pump A Control Valve Postion Switches | 1.0mm2 | 7C+E |  | TAS2-308-02 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA21AH010 (S020BFA10) | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21AH010 (S020BFA10) Fin Fan Cooler A MCC Cell | 1.0mm2 | 12C+E |  | TAS2-309-01, TAS2-311-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020NDA21AP010 (S020BFA10) | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21AP010 (S020BFA10) Acid Dilution SGW Pump A MCC Cell | 1.0mm2 | 12C+E |  | TAS2-308-01, TAS2-311-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020NDA21CF010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21CF010 Acid Dilution SGW Pump A Outlet Flow | 1.5mm2 | 2Pair |  | TAS2-110-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA21CP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21CP010 Acid Dilution SGW Pump A Inlet Pressure | 1.5mm2 | 1Triple |  | TAS2-111-01 | 159.6 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020NDA21CP011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21CP011 Acid Dilution SGW Pump A Pressure | 1.5mm2 | 2Pair |  | TAS2-111-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA21CP020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21CP020 Acid Dilution SGW Pump B Inlet Pressure | 1.5mm2 | 1Triple |  | TAS2-111-01 | 159.6 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020NDA21CP021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21CP021 Acid Dilution SGW Pump B Pressure | 1.5mm2 | 2Pair |  | TAS2-210-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA21CT010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA21CT010 Acid Dilution SGW Pump A Inlet Temp | 1.5mm2 | 2Pair |  | TAS2-111-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA22AA023_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA22AA023_Y01 Acid Dilution SGW Pump B Control Valve Solenoid | 2.5mm2 | 2C+E |  | TAS2-412-01 | 159.6 | C&I Sep | u - Tinned PVC / PVC
S020NDA22AA023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA22AA023 Acid Dilution SGW Pump B Control Valve Postion Switches | 1.0mm2 | 7C+E |  | TAS2-408-02 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA22AH020 (S020BFA10) | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA22AH020 (S020BFA10) Fin Fan Cooler B MCC Cell | 1.0mm2 | 12C+E |  | TAS2-409-01, TAS2-412-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020NDA22AP020 (S020BFA10) | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA22AP020 (S020BFA10) Acid Dilution SGW Pump B MCC Cell | 1.0mm2 | 12C+E |  | TAS2-409-01, TAS2-412-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020NDA22CF020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA22CF020 Acid Dilution SGW Pump B Outlet Flow | 1.5mm2 | 2Pair |  | TAS2-211-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA22CT020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA22CT020 Acid Dilution SGW Pump B Inlet Temp | 1.5mm2 | 2Pair |  | TAS2-201-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA23AA010_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA23AA010_Y01 HP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-510-01 | 123.9 | C&I Sep | u - Tinned PVC / PVC
S020NDA23AA010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA23AA010 HP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-112-02 | 123.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA23AA014_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA23AA014_Y01 HP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-510-01 | 123.9 | C&I Sep | u - Tinned PVC / PVC
S020NDA23AA014 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA23AA014 HP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-112-02 | 123.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA23CF011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA23CF011 HP SGW Sampling Flow | 1.5mm2 | 2Pair |  | TAS2-107-01 | 123.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA23CP511 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA23CP511 HP SGW Sampling Diff Pressure | 1.5mm2 | 2Pair |  | TAS2-107-01 | 123.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA23CP521 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA23CP521 HP SGW Sampling Diff Pressure | 1.5mm2 | 2Pair |  | TAS2-207-01 | 123.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA23CQ010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA23CQ010 HP SGW Sampling pH | 1.5mm2 | 2Pair |  | TAS2-110-01 | 123.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA23CT011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA23CT011 HP SGW Sampling Temp | 1.5mm2 | 2Pair |  | TAS2-107-01 | 123.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA24AA020_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA24AA020_Y01 HP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-610-01 | 123.9 | C&I Sep | u - Tinned PVC / PVC
S020NDA24AA020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA24AA020 HP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-212-02 | 123.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA24AA024_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA24AA024_Y01 HP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-212-02 | 123.9 | C&I Sep | u - Tinned PVC / PVC
S020NDA24AA024 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA24AA024 HP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-212-02 | 123.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA24CF020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA24CF020 HP SGW Sampling Flow | 1.5mm2 | 2Pair |  | TAS2-209-01 | 123.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA24CQ020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA24CQ020 HP SGW Sampling pH | 1.5mm2 | 2Pair |  | TAS2-209-01 | 123.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA24CT021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA24CT021 HP SGW Sampling Temp | 1.5mm2 | 2Pair |  | TAS2-207-01 | 123.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30AA001 | S020NDA30AA093 IP EDV Outlet MOV | S020NDA30AA001 IP Separator Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA010 LP Separator A Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 144.9 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA011 | S020NDA30AA010 LP Separator A Outlet MOV | S020NDA30AA011 LP Separator A Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA013 | S020NDA30AA011 LP Separator A Outlet MOV | S020NDA30AA013 IP LCV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA020 | S020NDB10AA043 LP EDV Outlet MOV | S020NDA30AA020 LP Separator B Outlet MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA021 | S020NDA30AA020 LP Separator B Outlet MOV | S020NDA30AA021 LP Separator B Outlet MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA023 | S020NDA30AA013 IP LCV Outlet MOV | S020NDA30AA023 IP LCV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA033 | S020NDA30AA023 IP LCV Outlet MOV | S020NDA30AA033 IP LCV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA043 | S020NDA30AA033 IP LCV Outlet MOV | S020NDA30AA043 IP LCV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA053 | S020NDA30AA043 IP LCV Outlet MOV | S020NDA30AA053 IP MDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA054 | S020NDA30AA053 IP MDV Outlet MOV | S020NDA30AA054 IP MDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA063 | S020NDA30AA054 IP MDV Outlet MOV | S020NDA30AA063 IP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA073 | S020NDA30AA063 IP EDV Outlet MOV | S020NDA30AA073 IP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA083 | S020NDA30AA073 IP EDV Outlet MOV | S020NDA30AA083 IP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA093 | S020NDA30AA083 IP EDV Outlet MOV | S020NDA30AA093 IP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-13 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDA30AA110 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA110 IP Level Control Valve - LCV Position Switches | 1.0mm2 | 7C+E |  | TAS2-309-01 | 99.75 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA30AA110 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA110 IP Level Control Valve - LCV Position | 1.0mm2 | 4Pair |  | TAS2-301-01, TAS2-306-01 | 99.75 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30AA120 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA120 IP Level Control Valve - LCV Position Switches | 1.0mm2 | 7C+E |  | TAS2-410-02 | 99.75 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA30AA120 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA120 IP Level Control Valve - LCV Position | 1.0mm2 | 4Pair |  | TAS2-302-01, TAS2-307-01 | 99.75 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30AA130 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA130 IP Level Control Valve - LCV Position Switches | 1.0mm2 | 7C+E |  | TAS2-409-02 | 99.75 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA30AA130 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA130 IP Level Control Valve - LCV Position | 1.0mm2 | 4Pair |  | TAS2-401-01, TAS2-406-01 | 99.75 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30AA140 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA140 IP Level Control Valve - LCV Position Switches | 1.0mm2 | 7C+E |  | TAS2-410-02 | 99.75 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA30AA140 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA140 IP Level Control Valve - LCV Position | 1.0mm2 | 4Pair |  | TAS2-301-01, TAS2-306-01 | 99.75 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30AA150 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA150 IP Modulating Dump Valve - MDV Solenoid | 2.5mm2 | 2C+E |  | TAS2-411-02 | 90.3 | C&I Sep | u - Tinned PVC / PVC
S020NDA30AA150 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA150 IP Modulating Dump Valve - MDV Position Switches | 1.0mm2 | 7C+E |  | TAS2-409-02 | 90.3 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDA30AA150 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA150 IP Modulating Dump Valve - MDV Position | 1.0mm2 | 4Pair |  | TAS2-401-01, TAS2-406-01 | 90.3 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30AA160 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA160 IP emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-303-01, TAS2-305-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30AA170 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA170 IP emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-303-01, TAS2-305-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30AA180 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA180 IP emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-403-01, TAS2-405-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30AA190 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30AA190 IP emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-403-01, TAS2-405-01 | 102.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30CL021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30CL021 LP SGW Drum Level | 1.5mm2 | 2Pair |  | TAS2-108-01 | 93.45 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30CL022 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30CL022 LP SGW Drum Level | 1.5mm2 | 2Pair |  | TAS2-109-01 | 93.45 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30CL023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30CL023 LP SGW Drum Level | 1.5mm2 | 2Pair |  | TAS2-208-01 | 93.45 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30CP011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30CP011 LP Separator A Inlet Pressure | 1.5mm2 | 2Pair |  | TAS2-108-01 | 70.35 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDA30CP012 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDA30CP012 LP Separator B Inlet Pressure | 1.5mm2 | 2Pair |  | TAS2-208-01 | 97.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB10AA001 | S020NDA30AA021 LP Separator B Outlet MOV | S020NDB10AA001 LP Separator Outlet MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDB10AA013 | S020NDB10AA054 LP MDV Outlet MOV | S020NDB10AA013 LP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDB10AA023 | S020NDB10AA013 LP EDV Outlet MOV | S020NDB10AA023 LP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDB10AA033 | S020NDB10AA023 LP EDV Outlet MOV | S020NDB10AA033 LP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDB10AA043 | S020NDB10AA033 LP EDV Outlet MOV | S020NDB10AA043 LP EDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDB10AA053 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB10AA053 LP MDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-07 | 144.9 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDB10AA054 | S020NDB10AA053 LP MDV Outlet MOV | S020NDB10AA054 LP MDV Outlet MOV | 22AWG | 1Pair |  | TAS2-803-07 | 21 | C&I Sep | ES Cu - Tinned PE/CPE (Grey Profibus)
S020NDB10AA110 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB10AA110 LP Emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-303-01, TAS2-305-01 | 160.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB10AA120 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB10AA120 LP Emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-303-01, TAS2-305-01 | 160.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB10AA130 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB10AA130 LP Emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-403-01, TAS2-405-01 | 160.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB10AA140 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB10AA140 LP Emergency Dump Valve - EDV Position | 1.0mm2 | 4Pair |  | TAS2-403-01, TAS2-405-01 | 160.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB10AA150 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB10AA150 LP Modulating Dump Valve - MDV Solenoid | 2.5mm2 | 2C+E |  | TAS2-411-02 | 131.25 | C&I Sep | u - Tinned PVC / PVC
S020NDB10AA150 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB10AA150 LP Modulating Dump Valve - MDV Position Switches | 1.0mm2 | 7C+E |  | TAS2-409-01 | 131.25 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDB10AA150 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB10AA150 LP Modulating Dump Valve - MDV Position | 1.0mm2 | 4Pair |  | TAS2-401-01, TAS2-406-01 | 131.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB11AA010_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB11AA010_Y01 LP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-510-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020NDB11AA010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB11AA010 LP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-505-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDB11AA013_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB11AA013_Y01 LP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-510-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020NDB11AA013 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB11AA013 LP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-505-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDB11CF011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB11CF011 LP SGW Sampling Flow | 1.5mm2 | 2Pair |  | TAS2-111-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB11CQ010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB11CQ010 LP SGW Sampling pH | 1.5mm2 | 2Pair |  | TAS2-110-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB11CT011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB11CT011 LP SGW Sampling Temperature | 1.5mm2 | 2Pair |  | TAS2-108-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB12AA020_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB12AA020_Y01 LP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-610-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020NDB12AA020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB12AA020 LP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-604-01 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDB12AA023_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB12AA023_Y01 LP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-610-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020NDB12AA023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB12AA023 LP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-604-01 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDB12CF021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB12CF021 LP SGW Sampling Flow | 1.5mm2 | 2Pair |  | TAS2-210-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB12CQ020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB12CQ020 LP SGW Sampling pH | 1.5mm2 | 2Pair |  | TAS2-210-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB12CT021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB12CT021 LP SGW Sampling Temperature | 1.5mm2 | 2Pair |  | TAS2-208-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB13AA030_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB13AA030_Y01 LP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-610-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020NDB13AA030 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB13AA030 LP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-604-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDB13AA033_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB13AA033_Y01 LP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-610-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020NDB13AA033 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB13AA033 LP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-604-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDB13CF031 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB13CF031 LP SGW Sampling Flow | 1.5mm2 | 2Pair |  | TAS2-211-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB13CQ030 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB13CQ030 LP SGW Sampling pH | 1.5mm2 | 2Pair |  | TAS2-211-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB13CT031 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB13CT031 LP SGW Sampling Temperature | 1.5mm2 | 2Pair |  | TAS2-208-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB14AA040_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB14AA040_Y01 LP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-510-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020NDB14AA040 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB14AA040 LP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-507-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDB14AA043_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB14AA043_Y01 LP SGW Sampling ISO Solenoid | 2.5mm2 | 2C+E |  | TAS2-510-02 | 144.9 | C&I Sep | u - Tinned PVC / PVC
S020NDB14AA043 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB14AA043 LP SGW Sampling ISO Postion Switches | 1.0mm2 | 7C+E |  | TAS2-507-02 | 144.9 | C&I Sep | S Cu - Tinned PVC / PVC
S020NDB14CF041 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB14CF041 LP SGW Sampling Flow | 1.5mm2 | 2Pair |  | TAS2-108-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB14CQ040 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB14CQ040 LP SGW Sampling pH | 1.5mm2 | 2Pair |  | TAS2-108-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NDB14CT041 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020NDB14CT041 LP SGW Sampling Temperature | 1.5mm2 | 2Pair |  | TAS2-108-01 | 144.9 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM10CL010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM10CL010 Sulphuric Acid Storage Tank Level Indicator | 1.5mm2 | 2Pair |  | TAS2-110-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM10CL010 | S020QCM10CL010 Sulphuric Acid Storage Tank Level Indicator | S020QCM10CL010 Sulphuric Acid Storage Tank Level | 1.5mm2 | 2Pair |  | TAS2-110-01 | 26.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM10CL020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM10CL020 Sulphuric Acid Storage Tank Overfill Protection - Terminal Box | 1.0mm2 | 7C+E |  | TAS2-411-02, (*)CCI-DET-2720 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020QCM10CL020 | S020QCM10CL020 Sulphuric Acid Storage Tank Overfill Protection - Terminal Box | S020QCM10CL020 Sulphuric Acid Storage Tank Level Indicator | 1.5mm2 | 1Triple |  | (*)ELE-PLN-2810, (*)CCI-DET-2720 | 1 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020QCM10CL020 | S020QCM10CL020 Sulphuric Acid Storage Tank Overfill Protection - Terminal Box | S020QCM10CL020 Sulphuric Acid Storage Tank Sounder Beacon | 1.5mm2 | 1Triple |  | (*)ELE-PLN-2810, (*)CCI-DET-2720 | 1 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020QCM10CL020 | S020QCM10CL020 Sulphuric Acid Storage Tank Level | S020QCM10CL020 Sulphuric Acid Storage Tank Level Indicator | 1.5mm2 | 2Pair |  | (*)ELE-PLN-2810, (*)CCI-DET-2720 | 26.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM10CL020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM10CL020 Sulphuric Acid Storage Tank Level Indicator | 1.0mm2 | 4Pair |  | TAS2-210-01, (*)CCI-DET-2720 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM10CT010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM10CT010 Sulphuric Acid Storage Tank Temperature | 1.5mm2 | 1Triple |  | TAS2-103-01 | 159.6 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020QCM20AA005_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AA005_Y01 Acid Dosing Pump A Input Control Valve Solenoid | 2.5mm2 | 2C+E |  | TAS2-312-01 | 159.6 | C&I Sep | u - Tinned PVC / PVC
S020QCM20AA005 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AA005 Acid Dosing Pump A Input Control Valve - Postion Switches | 1.0mm2 | 7C+E |  | TAS2-308-02 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020QCM20AA011_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AA011_Y01 Acid Dosing Pump A Output Control Valve Solenoid | 2.5mm2 | 2C+E |  | TAS2-312-01 | 159.6 | C&I Sep | u - Tinned PVC / PVC
S020QCM20AA011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AA011 Acid Dosing Pump A Output Control Valve Postion Switches | 1.0mm2 | 7C+E |  | TAS2-308-02 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020QCM20AA013_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AA013_Y01 Acid Mixing Control Valve Solenoid | 2.5mm2 | 2C+E |  | TAS2-312-02 | 159.6 | C&I Sep | u - Tinned PVC / PVC
S020QCM20AA013 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AA013 Acid Mixing Control Valve Postion Switches | 1.0mm2 | 7C+E |  | TAS2-308-01 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020QCM20AA031_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AA031_Y01 Acid Dosing Pump A Bypass Control Valve Solenoid | 2.5mm2 | 2C+E |  | TAS2-312-01 | 159.6 | C&I Sep | u - Tinned PVC / PVC
S020QCM20AA031 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AA031 Acid Dosing Pump A Bypass Control Valve Postion Switches | 1.0mm2 | 7C+E |  | TAS2-308-02 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020QCM20AP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AP010 Acid Dosing Pump A Package | 1.0mm2 | 12C+E |  | TAS2-508-01 | 159.6 | C&I Sep | CS Cu - Tinned PVC / PVC
S020QCM20AP010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20AP010 Acid Dosing Pump A Speed Control | 1.5mm2 | 2Pair |  | TAS2-503-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM20CF010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20CF010 Acid Dosing Pump A Outlet Flow | 1.5mm2 | 2Pair |  | TAS2-110-01 | 128.1 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM20CP011 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20CP011 Acid Dosing Pump A Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-110-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM20CT010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM20CT010 Acid Dosing Pump A Outlet Temperature | 1.5mm2 | 1Triple |  | TAS2-101-01 | 159.6 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020QCM21AA015_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21AA015_Y01 Acid Dosing Pump B Input Control Valve Solenoid | 2.5mm2 | 2C+E |  | TAS2-412-01 | 159.6 | C&I Sep | u - Tinned PVC / PVC
S020QCM21AA015 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21AA015 Acid Dosing Pump B Input Control Valve Postion Switches | 1.0mm2 | 7C+E |  | TAS2-408-01 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020QCM21AA021_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21AA021_Y01 Acid Dosing Pump B Output Control Valve Solenoid | 2.5mm2 | 2C+E |  | TAS2-412-01 | 159.6 | C&I Sep | u - Tinned PVC / PVC
S020QCM21AA021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21AA021 Acid Dosing Pump B Output Control Valve Postion Switches | 1.0mm2 | 7C+E |  | TAS2-408-02 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020QCM21AA023_Y01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21AA023_Y01 Acid Mixing Control Valve Solenoid | 2.5mm2 | 2C+E |  | TAS2-412-02 | 159.6 | C&I Sep | u - Tinned PVC / PVC
S020QCM21AA023 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21AA023 Acid Mixing Control Valve Postion Switches | 1.0mm2 | 7C+E |  | TAS2-408-01 | 159.6 | C&I Sep | S Cu - Tinned PVC / PVC
S020QCM21AP020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21AP020 Acid Dosing Pump B Package | 1.0mm2 | 12C+E |  | TAS2-608-01 | 159.6 | C&I Sep | CS Cu - Tinned PVC / PVC
S020QCM21AP020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21AP020 Acid Dosing Pump B Speed Control | 1.5mm2 | 2Pair |  | TAS2-603-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM21CF020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21CF020 Acid Dosing Pump B Outlet Flow | 1.5mm2 | 2Pair |  | TAS2-210-01 | 128.1 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM21CP021 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21CP021 Acid Dosing Pump B Outlet Pressure | 1.5mm2 | 2Pair |  | TAS2-210-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM21CT020 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM21CT020 Acid Dosing Pump B Outlet Temperature | 1.5mm2 | 1Triple |  | TAS2-201-01 | 159.6 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020QCM30CL031 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM30CL031 Sulphuric Acid Dosing System Sump Pump Level Indicator | 1.5mm2 | 2Pair |  | TAS2-110-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM30CL031 | S020QCM30CL031 Sulphuric Acid Dosing System Sump Pump Level Indicator | S020QCM30CL031 Sulphuric Acid Dosing System Sump Pump Level | 1.5mm2 | 2Pair |  | TAS2-110-01 | 4 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM30CL032 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM30CL032 Sulphuric Acid Dosing System Sump Pump Level Indicator | 1.5mm2 | 2Pair |  | TAS2-210-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM30CL032 | S020QCM30CL032 Sulphuric Acid Dosing System Sump Pump Level Indicator | S020QCM30CL032 Sulphuric Acid Dosing System Sump Pump Level | 1.5mm2 | 2Pair |  | TAS2-210-01 | 4 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020QCM30CQ010 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020QCM30CQ010 Sulphuric Acid Dosing System Sump Pump pH | 1.5mm2 | 2Pair |  | TAS2-110-01 | 159.6 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020SAA10CT001 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020SAA10CT001 Control Room Temperature | 1.5mm2 | 1Triple |  | TAS2-104-01 | 10.5 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020SAA10CT002 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020SAA10CT002 Electrical Room Temperature | 1.5mm2 | 1Triple |  | TAS2-104-01 | 10.5 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020SAA10CT003 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020SAA10CT003 Battery Room Temperature | 1.5mm2 | 1Triple |  | TAS2-104-01 | 10.5 | C&I Sep | le ES Cu - Tinned PVC / PVC
S020SAA10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020SAA10 HVAC System A | 1.0mm2 | 12C+E |  | TAS2-506-02 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020SAA10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020SAA10 HVAC System A | 1.0mm2 | 12C+E |  | TAS2-606-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020SAA10 | S020CRS20 Separation Plant Server Cabinet HSW5 | S020SAA10 Building HVAC Services | 0.5mm2 | 4Pair |  | TAS2-805-01 | 39.9 | C&I Sep | Cu - CAT6 STP
S020SAB10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020SAB10 HVAC System B | 1.0mm2 | 12C+E |  | TAS2-606-02 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020SAB10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020SAB10 HVAC System B | 1.0mm2 | 12C+E |  | TAS2-606-02 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020SGY10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | S020SGY10 Fire Alarm System | 1.0mm2 | 12C+E |  | TAS2-606-01 | 39.9 | C&I Sep | CS Cu - Tinned PVC / PVC
S020SGY10 | S020CRS20 Separation Plant Server Cabinet HSW5 | S020SGY10 Fire Alarm Panel | 0.5mm2 | 4Pair |  | TAS2-805-01 | 39.9 | C&I Sep | Cu - CAT6 STP
V010CVA01 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | V010CVA01 Vent Station AI Junction Box | 1.0mm2 | 8Pair |  | - | 391.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010CVA02 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | V010CVA02 Vent Station AI Junction Box | 1.0mm2 | 8Pair |  | - | 391.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010CVA31 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | V010CVA31 Vent Station AO Junction Box | 1.0mm2 | 8Pair |  | - | 391.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010CVA32 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | V010CVA32 Vent Station AO Junction Box | 1.0mm2 | 8Pair |  | - | 391.65 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010CVA51 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | V010CVA51 Junction Box - Solenoids | 2.5mm2 | 12C+E |  | - | 391.65 | C&I Sep | Cu - Tinned PVC / PVC
V010CVA52 | S020CRA30 Separation Plant PLC Cabinet - TAS2 | V010CVA52 Junction Box - Solenoids | 2.5mm2 | 12C+E |  | - | 391.65 | C&I Sep | Cu - Tinned PVC / PVC
V010NAA10AA111 | V010CVA51 Junction Box - Solenoids | V010NAA10AA111 HP Rock Mufflers - PCV Solenoid | 2.5mm2 | 2C+E |  | TAS2-311-02 | 68.25 | C&I Sep | u - Tinned PVC / PVC
V010NAA10AA111 | V010CVA01 Vent Station AI Junction Box | V010NAA10AA111 HP Rock Mufflers - PCV Position | 1.5mm2 | 2Pair |  | TAS2-301-01, | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA10AA111 | V010CVA31 Vent Station AO Junction Box | V010NAA10AA111 HP Rock Mufflers - PCV Setpoint | 1.5mm2 | 2Pair |  | TAS2-306-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA10AA121 | V010CVA51 Junction Box - Solenoids | V010NAA10AA121 HP Rock Mufflers - PCV Solenoid | 2.5mm2 | 2C+E |  | TAS2-312-01 | 68.25 | C&I Sep | u - Tinned PVC / PVC
V010NAA10AA121 | V010CVA01 Vent Station AI Junction Box | V010NAA10AA121 HP Rock Mufflers - PCV Position | 1.5mm2 | 2Pair |  | TAS2-302-01, TAS2-307-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA10AA121 | V010CVA31 Vent Station AO Junction Box | V010NAA10AA121 HP Rock Mufflers - PCV Setpoint | 1.5mm2 | 2Pair |  | TAS2-307-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA10AA131 | V010CVA52 Junction Box - Solenoids | V010NAA10AA131 HP Rock Mufflers - PCV Solenoid | 2.5mm2 | 2C+E |  | TAS2-406-01 | 68.25 | C&I Sep | u - Tinned PVC / PVC
V010NAA10AA131 | V010CVA02 Vent Station AI Junction Box | V010NAA10AA131 HP Rock Mufflers - PCV Position | 1.5mm2 | 2Pair |  | TAS2-402-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA10AA131 | V010CVA32 Vent Station AO Junction Box | V010NAA10AA131 HP Rock Mufflers - PCV Setpoint | 1.5mm2 | 2Pair |  | TAS2-407-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA20AA111 | V010CVA51 Junction Box - Solenoids | V010NAA20AA111 IP Rock Mufflers - PCV Solenoid | 2.5mm2 | 2C+E |  | TAS2-312-01 | 68.25 | C&I Sep | u - Tinned PVC / PVC
V010NAA20AA111 | V010CVA01 Vent Station AI Junction Box | V010NAA20AA111 IP Rock Mufflers - PCV Position | 1.5mm2 | 2Pair |  | TAS2-302-01, TAS2-307-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA20AA111 | V010CVA31 Vent Station AO Junction Box | V010NAA20AA111 IP Rock Mufflers - PCV Setpoint | 1.5mm2 | 2Pair |  | TAS2-307-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA20AA121 | V010CVA52 Junction Box - Solenoids | V010NAA20AA121 IP Rock Mufflers - PCV Solenoid | 2.5mm2 | 2C+E |  | TAS2-412-01 | 68.25 | C&I Sep | u - Tinned PVC / PVC
V010NAA20AA121 | V010CVA02 Vent Station AI Junction Box | V010NAA20AA121 IP Rock Mufflers - PCV Position | 1.5mm2 | 2Pair |  | TAS2-402-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA20AA121 | V010CVA32 Vent Station AO Junction Box | V010NAA20AA121 IP Rock Mufflers - PCV Setpoint | 1.5mm2 | 2Pair |  | TAS2-407-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA40AA111 | V010CVA51 Junction Box - Solenoids | V010NAA40AA111 LP Rock Mufflers - PCV Solenoid | 2.5mm2 | 2C+E |  | TAS2-311-02 | 68.25 | C&I Sep | u - Tinned PVC / PVC
V010NAA40AA111 | V010CVA01 Vent Station AI Junction Box | V010NAA40AA111 LP Rock Mufflers - PCV Position | 1.5mm2 | 2Pair |  | TAS2-301-01, TAS2-306-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA40AA111 | V010CVA31 Vent Station AO Junction Box | V010NAA40AA111 LP Rock Mufflers - PCV Setpoint | 1.5mm2 | 2Pair |  | TAS2-306-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA40AA121 | V010CVA51 Junction Box - Solenoids | V010NAA40AA121 LP Rock Mufflers - PCV Solenoid | 2.5mm2 | 2C+E |  | TAS2-312-01 | 68.25 | C&I Sep | u - Tinned PVC / PVC
V010NAA40AA121 | V010CVA01 Vent Station AI Junction Box | V010NAA40AA121 LP Rock Mufflers - PCV Position | 1.5mm2 | 2Pair |  | TAS2-302-01, | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA40AA121 | V010CVA31 Vent Station AO Junction Box | V010NAA40AA121 LP Rock Mufflers - PCV Setpoint | 1.5mm2 | 2Pair |  | TAS2-307-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA40AA131 | V010CVA52 Junction Box - Solenoids | V010NAA40AA131 LP Rock Mufflers - PCV Solenoid | 2.5mm2 | 2C+E |  | TAS2-411-01 | 68.25 | C&I Sep | u - Tinned PVC / PVC
V010NAA40AA131 | V010CVA02 Vent Station AI Junction Box | V010NAA40AA131 LP Rock Mufflers - PCV Position | 1.5mm2 | 2Pair |  | TAS2-401-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA40AA131 | S020CRA30 Vent Station AO Junction Box | V010NAA40AA131 LP Rock Mufflers - PCV Setpoint | 1.5mm2 | 2Pair |  | TAS2-406-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA40AA141 | V010CVA52 Junction Box - Solenoids | V010NAA40AA141 LP Rock Mufflers - PCV Solenoid | 2.5mm2 | 2C+E |  | TAS2-412-01 | 68.25 | C&I Sep | u - Tinned PVC / PVC
V010NAA40AA141 | V010CVA02 Vent Station AI Junction Box | V010NAA40AA141 LP Rock Mufflers - PCV Position | 1.5mm2 | 2Pair |  | TAS2-402-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
V010NAA40AA141 | V010CVA32 Vent Station AO Junction Box | V010NAA40AA141 LP Rock Mufflers - PCV Setpoint | 1.5mm2 | 2Pair |  | TAS2-407-01 | 68.25 | C&I Sep | ESCS Cu - Tinned PVC / PVC
S020NAA10CP031 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA10CP031 HP Separator Out Steam Pressure | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 173 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA10CP032 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA10CP032 HP Separator Out Steam Pressure | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 173 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA10CP033 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA10CP033 HP Separator Out Steam Pressure | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 173 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA20CP031 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA20CP031 IP Separtor Out Steam Pressure | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 131 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA20CP032 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA20CP032 IP Separtor Out Steam Pressure | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 131 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA20CP033 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA20CP033 IP Separtor Out Steam Pressure | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 131 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA31CP031 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA31CP031 LP Steam Pressure Line A | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 121 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA31CP032 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA31CP032 LP Steam Pressure Line A | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 121 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA31CP033 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA31CP033 LP Steam Pressure Line A | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 121 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA32CP031 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA32CP031 LP Steam Pressure Line B | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 142 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA32CP032 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA32CP032 LP Steam Pressure Line B | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 142 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NAA32CP033 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NAA32CP033 LP Steam Pressure Line B | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 142 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA10CL011 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA10CL011 HP SGW Drum Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 215 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA10CL012 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA10CL012 HP SGW Drum Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 215 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA10CL013 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA10CL013 HP SGW Drum Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 215 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA10CL014 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA10CL014 HP SGW Loop Seal Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 215 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA20AA140KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20AA140KA01 HP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 184 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDA20AA150KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20AA150KA01 HP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 184 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDA20AA160KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20AA160KA01 HP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 184 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDA20CG011 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CG011 HP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 184 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDA20CG021 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CG021 HP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 184 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDA20CG031 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CG031 HP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 184 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDA20CL011 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CL011 IP SGW Drum Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 142 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA20CL012 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CL012 IP SGW Drum Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 142 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA20CL013 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CL013 IP SGW Drum Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 142 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA20CL014 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CL014 IP SGW Loop Seal Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 142 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA20CR001 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CR001 HP Corrosometer | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 184 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA20CR002 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CR002 HP Corrosometer | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 139 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA20CR003 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA20CR003 HP Corrosometer | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 139 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA30AA160KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30AA160KA01 IP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 105 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDA30AA170KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30AA170KA01 IP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 105 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDA30AA180KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30AA180KA01 IP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 105 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDA30AA190KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30AA190KA01 IP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 105 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDA30CG011 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CG011 IP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 105 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDA30CG021 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CG021 IP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 105 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDA30CG031 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CG031 IP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 105 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDA30CG041 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CG041 IP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 105 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDA30CL011 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CL011 LP SGW Drum Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 131 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA30CL012 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CL012 LP SGW Drum Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 131 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA30CL013 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CL013 LP SGW Drum Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 131 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA30CL014 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CL014 LP SGW Loop Seal A Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 131 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA30CL015 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CL015 LP SGW Loop Seal B Level | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 131 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDA30CR004 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDA30CR004 IP Corrosometer | 1.5mm2 | 2Pair |  | TABG-JEC-0-000-ELE-PLN-2810 | 100 | C&I Sep SIS | ESCS Cu - Tinned PVC / PVC
S020NDB10AA110KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDB10AA110KA01 LP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 163 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDB10AA120KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDB10AA120KA01 LP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 163 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDB10AA130KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDB10AA130KA01 LP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 163 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDB10AA140KA01 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDB10AA140KA01 LP Emergency Dump Valve - EDV Solenoid | 2.5mm2 | 2C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 163 | C&I Sep SIS | u - Tinned PVC / PVC
S020NDB10CG011 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDB10CG011 LP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 163 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDB10CG021 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDB10CG021 LP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 163 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDB10CG031 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDB10CG031 LP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 163 | C&I Sep SIS | S Cu - Tinned PVC / PVC
S020NDB10CG041 | S020CRA40 SIS PLC Cabinet - TAS4 | S020NDB10CG041 LP Emergency Dump Valve - EDV Position Switches | 1.0mm2 | 7C+E |  | TABG-JEC-0-000-ELE-PLN-2810 | 163 | C&I Sep SIS | S Cu - Tinned PVC / PVC
L190NDB10AA001 | P020NDB10AA140 SGW Pumps Bypass - MOV | L190NDB10AA001 SGW Cross Country Line A - MOV | 22AWG | 1Pair |  | TAS3-803-04 | 21 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
L190NDB10AA002 | L190NDB10AA001 SGW Cross Country Line A - MOV | L190NDB10AA002 SGW Cross Country Line A - MOV | 22AWG | 1Pair |  | TAS3-803-04 | 21 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
L200NDB10AA001 | L190NDB10AA002 SGW Cross Country Line A - MOV | L200NDB10AA001 SGW Cross Country Line B - MOV | 22AWG | 1Pair |  | TAS3-803-04 | 21 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
L200NDB10AA002 | L200NDB10AA001 SGW Cross Country Line B - MOV | L200NDB10AA002 SGW Cross Country Line B - MOV | 22AWG | 1Pair |  | TAS3-803-04 | 21 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
P020BAA10 | P020CRS10 Pump Station Server Cabinet - HSW10 | P020BAA10 11kV Switchboard IRIG-B Bus A | 1.5mm2 | 2Pair |  | TAS2-800-05 | 26.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020BAA10 | P020CRS10 Pump Station Server Cabinet - HSW10 | P020BAA10 11kV Switchboard IRIG-B Bus B | 1.5mm2 | 2Pair |  | TAS2-800-05 | 26.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020BBA10GS010Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS010Q01 SGW Pump Station 11kV Switchboard A - Bustie | 1.0mm2 | 12C+E |  | TAS3-506-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS020Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS020Q01 SGW Pump Station 11kV Switchboard A - Incomer | 1.0mm2 | 12C+E |  | TAS3-506-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS030Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS030Q01 SGW Pump Station 11kV Switchboard A - Unison Incomer | 1.0mm2 | 12C+E |  | TAS3-506-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS040Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS040Q01 SGW Pump Station 11kV Switchboard A - LST 1 Feeder | 1.0mm2 | 12C+E |  | TAS3-506-02 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS050Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS050Q01 SGW Pump Station 11kV Switchboard A - VSD A Feeder | 1.0mm2 | 12C+E |  | TAS3-506-02 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS110Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS110Q01 SGW Pump Station 11kV Switchboard B - Bustie | 1.0mm2 | 12C+E |  | TAS3-606-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS120Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS120Q01 SGW Pump Station 11kV Switchboard B - Incomer | 1.0mm2 | 12C+E |  | TAS3-606-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS130Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS130Q01 SGW Pump Station 11kV Switchboard B - Sep Plant Tx Feeder | 1.0mm2 | 12C+E |  | TAS3-606-02 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS140Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS140Q01 SGW Pump Station 11kV Switchboard B - LST 2 Feeder | 1.0mm2 | 12C+E |  | TAS3-606-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS150Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS150Q01 SGW Pump Station 11kV Switchboard B - VSD B Feeder | 1.0mm2 | 12C+E |  | TAS3-606-02 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10GS160Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BBA10GS160Q01 SGW Pump Station 11kV Switchboard B - VSD C Feeder | 1.0mm2 | 12C+E |  | TAS3-607-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BBA10HSW71 | P020CRS10HSW7 Pump Station Server Cabinet HSW7 | P020BBA10HSW71 11kV Switchboard Bus A - HSW71 | 50/125μm | MultimodePreformed |  | TAS3-804-01 | 26.25 | C&I SGW | imode Preformed Cable with LC Connectors
P020BBA10HSW81 | P020CRS10HSW8 Pump Station Server Cabinet HSW8 | P020BBA10HSW81 11kV Switchboard Bus B - HSW81 | 50/125μm | MultimodePreformed |  | TAS3-804-01 | 26.25 | C&I SGW | imode Preformed Cable with LC Connectors
P020BBA10HSW81 | P020BBA10HSW71 11kV Switchboard Bus A - HSW71 | P020BBA10HSW81 11kV Switchboard Bus B - HSW81 | 50/125μm | MultimodePreformed |  | TAS3-804-01 | 10 | C&I SGW | imode Preformed Cable with LC Connectors
P020BFA10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFA10 SGW Pump Station LV Switchboard | 1.0mm2 | 24C+E |  | TAS3-503-02 , TAS3-504-01 , TAS3-505-02 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFA10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFA10 SGW Pump Station LV Switchboard | 1.0mm2 | 24C+E |  | TAS3-603-02 , TAS3-604-01 , TAS3-609-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - GFHP Pump A | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - VSD Cooler A Fan 1 | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - VSD Cooler A Fan 2 | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - VSD Cooler B Fan 1 | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - VSD Cooler B Fan 2 | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - VSD Cooler C Fan 1 | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - VSD Cooler C Fan 2 | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - General Lighting and Power A | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - Process DB A | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - HVAC System A | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - 110VDC System A | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - UPS System B Bypass | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - Compressor A | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus A Feeder - Compressor A Dryer | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab GFHP A Motor Protecction Relay - GFHP Pump A | 0.5mm2 | 4Pair |  | TAS3-805-02 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - GFHP Pump B | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - VSD Cooler A Fan 3 | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - VSD Cooler A Fan 4 | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - VSD Cooler B Fan 3 | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - VSD Cooler B Fan 4 | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - VSD Cooler C Fan 3 | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - VSD Cooler C Fan 4 | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - General Lighting and Power B | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - Process DB B | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - HVAC System B | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - 110VDC System B | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - UPS System A Bypass | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW53 LV Switchboard - HSW53 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - Compressor B | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab LV Switchboard Bus B Feeder - Compressor B Dryer | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS00x0_Fab | P020BFA10HSW52 LV Switchboard - HSW52 | P020BFA10GS00x0_Fab GFHP B Motor Protecction Relay - GFHP Pump B | 0.5mm2 | 4Pair |  | TAS3-805-03 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS010_F02 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS010_F02 LV Switchboard Bus A - Bustie | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS010_F11 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS010_F11 LV Switchboard Bus B - Temp EDG Incomer | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS010Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFA10GS010Q01 SGW Pump Station LV Switchboard A - Bustie | 1.0mm2 | 12C+E |  | TAS3-504-01, TAS3-509-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFA10GS020_F02 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS020_F02 LV Switchboard Bus A - Incomer | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS020_F03 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS020_F03 LV Switchboard Bus A - Incomer Backup Protection | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS020_F03 | P020CRS10HSW7 Pump Station Server Cabinet HSW7 | P020BFA10GS020_F03 LV Switchboard Bus A - Incomer Backup Protection Relay | 50/125μm | MultimodePreformed |  | TAS3-804-01 | 30 | C&I SGW | imode Preformed Cable with LC Connectors
P020BFA10GS020_F11 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS020_F11 LV Switchboard Bus A - Temp EDG Incomer | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS020_PQM1 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS020_PQM1 LV Switchboard Bus A - Incomer PQM | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS020_PQM2 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS020_PQM2 LV Switchboard Bus A - Temp Incomer PQM | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS020Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFA10GS020Q01 SGW Pump Station LV Switchboard A - Incomer | 1.0mm2 | 12C+E |  | TAS3-504-01, TAS3-509-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFA10GS110_F02 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS110_F02 LV Switchboard Bus B - Bustie | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS110Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFA10GS110Q01 SGW Pump Station LV Switchboard B - Bustie | 1.0mm2 | 12C+E |  | TAS3-604-01, TAS3-609-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFA10GS120_F02 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS120_F02 LV Switchboard Bus B - Incomer | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS120_F03 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS120_F03 LV Switchboard Bus B - Incomer Backup Protection | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS120_F03 | P020CRS10HSW8 Pump Station Server Cabinet HSW8 | P020BFA10GS120_F03 LV Switchboard Bus B - Incomer Backup Protection Relay | 50/125μm | MultimodePreformed |  | TAS3-804-01 | 30 | C&I SGW | imode Preformed Cable with LC Connectors
P020BFA10GS120_PQM1 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS120_PQM1 LV Switchboard Bus B - PQM | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS120_PQM2 | P020BFA10HSW51 LV Switchboard - HSW51 | P020BFA10GS120_PQM2 LV Switchboard Bus B - Temp Incomer PQM | 0.5mm2 | 4Pair |  | TAS3-805-04 |  | C&I SGW | Cu - CAT6 STP
P020BFA10GS120Q01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFA10GS120Q01 SGW Pump Station LV Switchboard B - Incomer | 1.0mm2 | 12C+E |  | TAS3-604-01, TAS3-609-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFA10HSW51 | P020CRS10HSW5 Pump Station Server Cabinet HSW5 | P020BFA10HSW51 LV Switchboard - HSW51 | 0.5mm2 | 4Pair |  | TAS3-805-01 | 30 | C&I SGW | Cu - CAT6 STP
P020BFA10HSW52 | P020CRS10HSW5 Pump Station Server Cabinet HSW5 | P020BFA10HSW52 LV Switchboard - HSW52 | 0.5mm2 | 4Pair |  | TAS3-805-01 | 30 | C&I SGW | Cu - CAT6 STP
P020BFA10HSW53 | P020CRS10HSW5 Pump Station Server Cabinet HSW5 | P020BFA10HSW53 LV Switchboard - HSW53 | 0.5mm2 | 4Pair |  | TAS3-805-01 | 30 | C&I SGW | Cu - CAT6 STP
P020BFA10 | P020CRS10 Pump Station Server Cabinet - HSW10 | P020BFA10 LV Switchboard IRIG-B | 1.5mm2 | 2Pair |  | TAS2-800-05 | 26.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020BFE10GT010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFE10GT010 SGW Pump Station VSD A Transformer | 1.0mm2 | 12C+E |  | TAS3-504-02 | 57.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFE10GT020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFE10GT020 SGW Pump Station VSD B Transformer | 1.0mm2 | 12C+E |  | TAS3-604-02 | 57.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFE10GT030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFE10GT030 SGW Pump Station VSD C Transformer | 1.0mm2 | 12C+E |  | TAS3-607-02 | 57.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFT10GT010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFT10GT010 Pump Station Local Services Transformer 1 | 1.0mm2 | 12C+E |  | TAS3-504-02 | 57.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BFT10GT020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BFT10GT020 Pump Station Local Services Transformer 2 | 1.0mm2 | 12C+E |  | TAS3-604-02 | 57.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BRA10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BRA10 230VAC Inverter A | 1.0mm2 | 12C+E |  | TAS3-507-01 | 15.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BRA10 | P020CRS10 Pump Station Server Cabinet HSW5 | P020BRA10 230VAC Inverter A | 0.5mm2 | 4Pair |  | TAS3-805-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020BRA10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BRA10 230VAC Inverter A | 1.0mm2 | 12Pair |  | TAS3-502-01 | 15.75 | C&I SGW | r ESCS Cu - Tinned PVC / PVC
P020BRB10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BRB10 230VAC Inverter B | 1.0mm2 | 12C+E |  | TAS3-607-02 | 15.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BRB10 | P020CRS10 Pump Station Server Cabinet HSW5 | P020BRB10 230VAC Inverter B | 0.5mm2 | 4Pair |  | TAS3-805-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020BRB10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BRB10 230VAC Inverter B | 1.0mm2 | 12Pair |  | TAS3-602-01 | 15.75 | C&I SGW | r ESCS Cu - Tinned PVC / PVC
P020BTL10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BTL10 110VDC Power Supply System A | 1.0mm2 | 12C+E |  | TAS3-507-01 | 15.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BTL10 | P020CRS10 Pump Station Server Cabinet HSW5 | P020BTL10 110VDC System A | 0.5mm2 | 4Pair |  | TAS3-805-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020BTL10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BTL10 110VDC Power Supply System A | 1.0mm2 | 12Pair |  | TAS3-502-01 | 15.75 | C&I SGW | r ESCS Cu - Tinned PVC / PVC
P020BTM10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BTM10 110VDC Power Supply System B | 1.0mm2 | 12C+E |  | TAS3-607-01 | 15.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020BTM10 | P020CRS10 Pump Station Server Cabinet HSW5 | P020BTM10 110VDC System B | 0.5mm2 | 4Pair |  | TAS3-805-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020BTM10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020BTM10 110VDC Power Supply System B | 1.0mm2 | 12Pair |  | TAS3-602-01 | 15.75 | C&I SGW | r ESCS Cu - Tinned PVC / PVC
P020CRA10 | - Tauhara Power Plant | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 1 | 1.5mm2 | 19C |  | - | 299.25 | C&I SGW | #NAME?
P020CRA10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 2 | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 1 | 1.5mm2 | 19C |  | - | 543.9 | C&I SGW | #NAME?
P020CRA10 | - Tauhara Power Plant | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 1 | 1.5mm2 | 12Pair |  | - | 299.25 | C&I SGW | r CS Cu - Tinned PVC / PVC
P020CRA10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 2 | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 1 | 1.5mm2 | 12Pair |  | - | 543.9 | C&I SGW | r CS Cu - Tinned PVC / PVC
P020CRA10 | P020CRS10 Pump Station Server Cabinet | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 1 | 0.5mm2 | 4Pair |  | TAS3-802-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020CRA10 | P020CRS10 Pump Station Server Cabinet | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 1 | 0.5mm2 | 4Pair |  | TAS3-802-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020CRA10 | P020CRS10 Pump Station Server Cabinet | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 2 | 0.5mm2 | 4Pair |  | TAS3-802-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020CRA10 | P020CRS10 Pump Station Server Cabinet | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 2 | 0.5mm2 | 4Pair |  | TAS3-802-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020CRA10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020CRA10 Pump Station PLC Cabinet - HSW41 | 0.5mm2 | 4Pair |  | TAS2-800-05 |  | C&I SGW | Cu - CAT6 STP
P020CRA10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020CRA10 Pump Station PLC Cabinet - HSW41 | 0.5mm2 | 4Pair |  | TAS2-800-05 |  | C&I SGW | Cu - CAT6 STP
P020CRA10 | - Tauhara Power Plant | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 1 | 1.5mm2 | 12Pair |  | TAS3-602-01 | 299.25 | C&I SGW | r ESCS Cu - Tinned PVC / PVC
P020CRA10 | S020CRA30 Separation Plant PLC Cabinet - TAS2 CPU 2 | P020CRA10 Pump Station PLC Cabinet - TAS3 CPU 1 | 1.5mm2 | 12Pair |  | - | 543.9 | C&I SGW | r ESCS Cu - Tinned PVC / PVC
P020CRS10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020CRS10 Server Cabinet NSP | 1.0mm2 | 24C+E |  | TAS3-603-01 | 15.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020CRS10HSW5 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020CRS10HSW5 Pump Station Server Cabinet HSW5 | 0.5mm2 | 4Pair |  | TAS3-805-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020CRS10 | - Tauhara Power Plant | P020CRS10 Pump Station Server Cabinet NSP | 9/125μm | 96Core |  | (*)CCI-SDG-1805 | 299.25 | C&I SGW | re Singlemode OS2 PE Outdoor Jacket
P020CRS10 | P020CRS10 Pump Station Server Cabinet | P020CRS10 Pump Station Server Cabinet - VM Host 2 | 0.5mm2 | 4Pair |  | TAS3-802-02 |  | C&I SGW | Cu - CAT6 STP
P020CRS10 | P020CRS10 Pump Station Server Cabinet | P020CRS10 Pump Station Server Cabinet - VM Host 2 | 0.5mm2 | 4Pair |  | TAS3-802-02 |  | C&I SGW | Cu - CAT6 STP
P020CRS10 | P020CRS10 Pump Station Server Cabinet | P020CRS10 Pump Station Server Cabinet - VM Host 2 | 0.5mm2 | 4Pair |  | TAS3-802-02 |  | C&I SGW | Cu - CAT6 STP
P020CRS10 | P020CRS10 Pump Station Server Cabinet | P020CRS10 Pump Station Server Cabinet - VM Host 2 | 0.5mm2 | 4Pair |  | TAS3-802-02 |  | C&I SGW | Cu - CAT6 STP
P020CRS10 | P020CRS10 Pump Station Server Cabinet | P020CRS10 Pump Station Server Cabinet - VM Host 2 | 0.5mm2 | 4Pair |  | TAS3-802-02 |  | C&I SGW | Cu - CAT6 STP
P020CRS10 | P020CRS10 Pump Station Server Cabinet | P020CRS10 Pump Station Server Cabinet - VM Host 2 | 0.5mm2 | 4Pair |  | TAS3-802-02 |  | C&I SGW | Cu - CAT6 STP
P020CRS10 | P020CRA10 Pump Station PLC Cabinet - VC-8000 | P020CRS10 Pump Station Server Cabinet - HSW10 | 0.5mm2 | 4Pair |  | TAS3-820-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020CRS10 | P020CRA10 Pump Station PLC Cabinet - HSW41 | P020CRS10 Pump Station Server Cabinet - MC21 | 0.5mm2 | 4Pair |  | TAS2-800-05, TAS3-820-01 | 15.75 | C&I SGW | Cu - CAT6 STP
P020CRS10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020CRS10 Server Cabinet NSP | 1.0mm2 | 4Pair |  | TAS3-601-01 | 15.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020CRS30 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020CRS30 Server Cabinet Building Services | 1.0mm2 | 12C+E |  | TAS3-505-02 | 15.75 | C&I SGW | CS Cu - Tinned PVC / PVC
P020CRS30 | P020CRS10 Pump Station Server Cabinet NSP | P020CRS30 Pump Station Server Cabinet Building Services | 9/125μm | 24Core |  | (*)CCI-SDG-1804 | 10.5 | C&I SGW | re Singlemode OS2
P020CRS30 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020CRS30 Server Cabinet Building Services | 1.0mm2 | 4Pair |  | TAS3-601-01 | 15.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020CRU10 | P020CRS10 Pump Station Server Cabinet | P020CRU10 OWS | 0.5mm2 | 4Pair |  | TAS3-802-02 | 15.75 | C&I SGW | Cu - CAT6 STP
P020CRU10 | P020CRS10 Pump Station Server Cabinet | P020CRU10 OWS | 0.5mm2 | 4Pair |  | TAS3-802-02 | 26.25 | C&I SGW | Cu - CAT6 STP
P020CVA01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020CVA01 GFHP Leak Detection JB | 1.5mm2 | 12Pair |  | TAS3-106-01, TAS3-107-01, TAS3-206-01, TAS3-207-01 | 204.75 | C&I SGW | r ESCS Cu - Tinned PVC / PVC
P020CVA41 | P020NDB10AP010_U01 SGW Pump A VSD | P020CVA41 SGW Pump RTD Junction Box | 1.0mm2 | 12Triple |  | (*)ELE-SDG-1144 | 84 | C&I SGW | ple ESCS Cu - Tinned PVC / PVC
P020CVA42 | P020NDB10AP020_U01 SGW Pump B VSD | P020CVA42 SGW Pump RTD Junction Box | 1.0mm2 | 12Triple |  | (*)ELE-SDG-1144 | 84 | C&I SGW | ple ESCS Cu - Tinned PVC / PVC
P020CVA43 | P020NDB10AP030_U01 SGW Pump C VSD | P020CVA43 SGW Pump RTD Junction Box | 1.0mm2 | 12Triple |  | (*)ELE-SDG-1144 | 84 | C&I SGW | ple ESCS Cu - Tinned PVC / PVC
P020CVA44 | P020LFC20AP010 GFHP Pump A - MCC Cell | P020CVA44 GFHP Pump RTD Junction Box | 1.0mm2 | 12Triple |  | (*)ELE-SDG-1132 | 173.25 | C&I SGW | ple ESCS Cu - Tinned PVC / PVC
P020CVA45 | P020LFC20AP020 GFHP Pump B - MCC Cell | P020CVA45 GFHP Pump RTD Junction Box | 1.0mm2 | 12Triple |  | (*)ELE-SDG-1132 | 173.25 | C&I SGW | ple ESCS Cu - Tinned PVC / PVC
P020CVA46 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020CVA46 SGW Pump RTD Junction Box | 1.0mm2 | 12Triple |  | TAS3-101-01, TAS3-102-01, TAS3-103-01, TAS3-202-01 | 89 | C&I SGW | ple ESCS Cu - Tinned PVC / PVC
P020CVA47 | P020NAB10AP010_U01 Condensate Pump A VSD | P020CVA47 Condensate Pump RTD Junction Box | 1.0mm2 | 12Triple |  | (*)ELE-SDG-1142 | 94.5 | C&I SGW | ple ESCS Cu - Tinned PVC / PVC
P020GWA20CL010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA20CL010 Seal Water Tank 1 - Level Indicator | 1.5mm2 | 2Pair |  | TAS3-105-01 | 78.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA20CL010 | P020GWA20CL010 Seal Water Tank 1 - Level Indicator | P020GWA20CL010 Seal Water Tank 1 - Level | 1.5mm2 | 2Pair |  | TAS3-105-01 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA20CL011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA20CL011 Seal Water Tanks Bund - Level Indicator | 1.5mm2 | 2Pair |  | TAS3-205-01 | 78.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA20CL011 | P020GWA20CL011 Seal Water Tanks Bund - Level Indicator | P020GWA20CL011 Seal Water Tanks Bund - Level | 1.5mm2 | 2Pair |  | TAS3-205-01 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA20CL020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA20CL020 Seal Water Tank 2 - Level Indicator | 1.5mm2 | 2Pair |  | TAS3-205-01 | 78.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA20CL020 | P020GWA20CL020 Seal Water Tank 2 - Level Indicator | P020GWA20CL020 Seal Water Tank 2 - Level | 1.5mm2 | 2Pair |  | TAS3-205-01 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA21AA011_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA21AA011_Y01 Seal Water CV - Solenoid | 2.5mm2 | 2C+E |  | TAS3-307-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020GWA21AA011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA21AA011 Seal Water CV - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-306-02 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA21AA016_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA21AA016_Y01 Seal Water CV - Solenoid | 2.5mm2 | 2C+E |  | TAS3-407-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020GWA21AA016 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA21AA016 Seal Water CV - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-406-02 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA21CP001 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA21CP001 Seal Water Inline Filter Diff - Pressure | 1.5mm2 | 2Pair |  | TAS3-207-01 | 31.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA21CP002 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA21CP002 Seal Water - Pressure | 1.5mm2 | 2Pair |  | TAS3-107-01 | 31.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA22AA021_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA22AA021_Y01 Seal Water Pump A Outlet CV - Solenoid | 2.5mm2 | 2C+E |  | TAS3-307-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020GWA22AA021 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA22AA021 Seal Water Pump A Outlet CV - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-306-02 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA22AP010_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA22AP010_U01 Seal Water Pump A VSD | 1.0mm2 | 12C+E |  | TAS3-304-02 , TAS3-308-02 | 21 | C&I SGW | CS Cu - Tinned PVC / PVC
P020GWA22AP010_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA22AP010_U01 Seal Water Pump A VSD | 1.5mm2 | 2Pair |  | TAS3-302-01 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA22AP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA22AP010 Seal Water Pump A VSD | 980/1000μm | ABBTK811VO50 |  | TAS3-806-01 | 21 | C&I SGW | B TK811VO50 POF Cable Duplex Male Connectors
P020GWA22CP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA22CP010 Seal Water Pump A Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-106-01 | 31.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA23AA031_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA23AA031_Y01 Seal Water Pump B Outlet CV - Solenoid | 2.5mm2 | 2C+E |  | TAS3-308-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020GWA23AA031 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA23AA031 Seal Water Pump B Outlet CV - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-306-02 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA23AP020_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA23AP020_U01 Seal Water Pump B VSD | 1.0mm2 | 12C+E |  | TAS3-303-01 , TAS3-309-01 | 21 | C&I SGW | CS Cu - Tinned PVC / PVC
P020GWA23AP020_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA23AP020_U01 Seal Water Pump B VSD | 1.5mm2 | 2Pair |  | TAS3-303-02 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA23AP020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA23AP020 Seal Water Pump B VSD | 980/1000μm | ABBTK811VO50 |  | TAS3-806-01 | 21 | C&I SGW | B TK811VO50 POF Cable Duplex Male Connectors
P020GWA23CP020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA23CP020 Seal Water Pump B Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-107-01 | 31.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA24AA041_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA24AA041_Y01 Seal Water Pump C Outlet CV - Solenoid | 2.5mm2 | 2C+E |  | TAS3-407-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020GWA24AA041 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA24AA041 Seal Water Pump C Outlet CV - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-406-02 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA24AP030_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA24AP030_U01 Seal Water Pump C VSD | 1.0mm2 | 12C+E |  | TAS3-404-02 , TAS3-409-02 | 21 | C&I SGW | CS Cu - Tinned PVC / PVC
P020GWA24AP030_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA24AP030_U01 Seal Water Pump C VSD | 1.5mm2 | 2Pair |  | TAS3-402-01 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA24AP030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA24AP030 Seal Water Pump C VSD | 980/1000μm | ABBTK811VO50 |  | TAS3-806-02 | 21 | C&I SGW | B TK811VO50 POF Cable Duplex Male Connectors
P020GWA24CP030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA24CP030 Seal Water Pump C Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-207-01 | 31.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA30AA051_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA30AA051_Y01 SGW Pump A Seal Water CV Inlet - Solenoid | 2.5mm2 | 2C+E |  | TAS3-307-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA30AA051 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA30AA051 SGW Pump A Seal Water CV Inlet - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-111-01 | 84 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA30AA054_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA30AA054_Y01 SGW Pump A Seal Water CV Outlet - Solenoid | 2.5mm2 | 2C+E |  | TAS3-307-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA30AA054 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA30AA054 SGW Pump A Seal Water CV Outlet - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-111-01 | 84 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA30CF010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA30CF010 SGW Pump A Seal Water Inlet - Flow | 2.5mm2 | 2C+E |  | TAS3-108-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA30CF010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA30CF010 SGW Pump A Seal Water Inlet - Flow | 1.5mm2 | 2Pair |  | TAS3-108-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA30CF011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA30CF011 SGW Pump A Seal Water Inlet - Flow | 2.5mm2 | 2C+E |  | TAS3-108-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA30CF011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA30CF011 SGW Pump A Seal Water Inlet - Flow | 1.5mm2 | 2Pair |  | TAS3-108-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA30CT010 | P020CVA46 SGW Pump RTD Junction Box | P020GWA30CT010 SGW Pump A Seal Water Outlet - Temperature | 1.5mm2 | 1Triple |  | TAS3-101-01 | 31.5 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020GWA30CT050 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA30CT050 Seal Water Return Fin Fan Cooler - Temp | 1.5mm2 | 1Triple |  | TAS3-101-01 | 78.75 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020GWA31AA061_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA31AA061_Y01 SGW Pump B Seal Water CV Inlet - Solenoid | 2.5mm2 | 2C+E |  | TAS3-307-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA31AA061 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA31AA061 SGW Pump B Seal Water CV Inlet - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-211-01 | 84 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA31AA064_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA31AA064_Y01 SGW Pump B Seal Water CV Outlet - Solenoid | 2.5mm2 | 2C+E |  | TAS3-307-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA31AA064 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA31AA064 SGW Pump B Seal Water CV Outlet - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-211-01 | 84 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA31CF020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA31CF020 SGW Pump B Seal Water Inlet - Flow | 2.5mm2 | 2C+E |  | TAS3-107-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA31CF020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA31CF020 SGW Pump B Seal Water Inlet - Flow | 1.5mm2 | 2Pair |  | TAS3-107-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA31CF021 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA31CF021 SGW Pump B Seal Water Inlet - Flow | 2.5mm2 | 2C+E |  | TAS3-107-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA31CF021 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA31CF021 SGW Pump B Seal Water Inlet - Flow | 1.5mm2 | 2Pair |  | TAS3-107-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA31CT020 | P020CVA46 SGW Pump RTD Junction Box | P020GWA31CT020 SGW Pump B Seal Water Outlet - Temperature | 1.5mm2 | 1Triple |  | TAS3-103-01 | 21 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020GWA32AA071_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA32AA071_Y01 SGW Pump C Seal Water CV Inlet - Solenoid | 2.5mm2 | 2C+E |  | TAS3-407-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA32AA071 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA32AA071 SGW Pump C Seal Water CV Inlet - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-404-02 | 84 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA32AA074_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA32AA074_Y01 SGW Pump C Seal Water CV Outlet - Solenoid | 2.5mm2 | 2C+E |  | TAS3-407-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA32AA074 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA32AA074 SGW Pump C Seal Water CV Outlet - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-404-02 | 84 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA32CF030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA32CF030 SGW Pump C Seal Water Inlet - Flow | 2.5mm2 | 2C+E |  | TAS3-207-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA32CF030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA32CF030 SGW Pump C Seal Water Inlet - Flow | 1.5mm2 | 2Pair |  | TAS3-207-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA32CF031 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA32CF031 SGW Pump C Seal Water Inlet - Flow | 2.5mm2 | 2C+E |  | TAS3-207-01 | 84 | C&I SGW | u - Tinned PVC / PVC
P020GWA32CF031 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA32CF031 SGW Pump C Seal Water Inlet - Flow | 1.5mm2 | 2Pair |  | TAS3-207-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA32CT030 | P020CVA46 SGW Pump RTD Junction Box | P020GWA32CT030 SGW Pump C Seal Water Outlet - Temperature | 1.5mm2 | 1Triple |  | TAS3-202-01 | 31.5 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020GWA33AA081_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33AA081_Y01 Condensate Pump Seal Water CV Inlet - Solenoid | 2.5mm2 | 2C+E |  | TAS3-407-01 | 94.5 | C&I SGW | u - Tinned PVC / PVC
P020GWA33AA081 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33AA081 Condensate Pump Seal Water CV Inlet - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-405-02 | 94.5 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA33AA084_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33AA084_Y01 Condensate Pump Seal Water CV Outlet - Solenoid | 2.5mm2 | 2C+E |  | TAS3-407-01 | 94.5 | C&I SGW | u - Tinned PVC / PVC
P020GWA33AA084 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33AA084 Condensate Pump Seal Water CV Outlet - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-405-02 | 94.5 | C&I SGW | S Cu - Tinned PVC / PVC
P020GWA33AH010_M01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33AH010_M01 Seal Water Return Fin Fan Cooler - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-02, TAS3-304-02, TAS3-305-02, TAS3-309-02 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020GWA33CF040 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33CF040 Condensate Pump A Seal Water Inlet - Flow | 2.5mm2 | 2C+E |  | TAS3-208-01 | 94.5 | C&I SGW | u - Tinned PVC / PVC
P020GWA33CF040 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33CF040 Condensate Pump A Seal Water Inlet - Flow | 1.5mm2 | 2Pair |  | TAS3-208-01 | 94.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA33CF041 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33CF041 Condensate Pump A Seal Water Inlet - Flow | 2.5mm2 | 2C+E |  | TAS3-208-01 | 94.5 | C&I SGW | u - Tinned PVC / PVC
P020GWA33CF041 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33CF041 Condensate Pump A Seal Water Inlet - Flow | 1.5mm2 | 2Pair |  | TAS3-208-01 | 94.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020GWA33CT040 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020GWA33CT040 Condensate Pump Seal Water Outlet - Temperature | 1.5mm2 | 1Triple |  | TAS3-203-01 | 94.5 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LCF20CT012 | P020CVA44 GFHP Pump RTD Junction Box | P020LCF20CT012 GFHP Pump A Stator 1 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LCF20CT023 | P020CVA45 GFHP Pump RTD Junction Box | P020LCF20CT023 GFHP Pump B Stator 2 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LCF20CT025 | P020CVA45 GFHP Pump RTD Junction Box | P020LCF20CT025 GFHP Pump B NDE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20AA010 | P020NAB10AA110 Condensate Pumps Bypass - MOV | P020LFC20AA010 GFHP Pump A Outlet - MOV | 22AWG | 1Pair |  | TAS3-803-05 | 94.5 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
P020LFC20AA020 | P020LFC20AA010 GFHP Pump A Outlet - MOV | P020LFC20AA020 GFHP Pump B Outlet - MOV | 22AWG | 1Pair |  | TAS3-803-05 | 21 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
P020LFC20AP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20AP010 GFHP Pump A MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-01, TAS3-304-01, TAS3-305-01, TAS3-309-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020LFC20AP020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20AP020 GFHP Pump B MCC Cell | 1.0mm2 | 12C+E |  | TAS3-403-01 , TAS3-404-01 , TAS3-405-01 , TAS3-409-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020LFC20CF010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CF010 GFHP Pump Station Outlet - Flow | 1.5mm2 | 2Pair |  | TAS3-206-01 | 204.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL001 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CL001 Geothermal Fluid Holding Pond - Level Indicator | 1.5mm2 | 2Pair |  | TAS3-106-01 | 204.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL001 | P020LFC20CL001 Geothermal Fluid Holding Pond - Level Indicator | P020LFC20CL001 Geothermal Fluid Holding Pond - Level | 1.5mm2 | 2Pair |  | TAS3-106-01 | 10 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL002 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CL002 Geothermal Fluid Holding Pond - Level Indicator | 1.5mm2 | 2Pair |  | TAS3-206-01 | 204.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL002 | P020LFC20CL002 Geothermal Fluid Holding Pond - Level Indicator | P020LFC20CL002 Geothermal Fluid Holding Pond - Level | 1.5mm2 | 2Pair |  | TAS3-206-01 | 10 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL003 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CL003 Geothermal Fluid Holding Pond - Level Indicator | 1.5mm2 | 2Pair |  | TAS3-109-01 | 204.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL003 | P020LFC20CL003 Geothermal Fluid Holding Pond - Level Indicator | P020LFC20CL003 Geothermal Fluid Holding Pond - Level | 1.5mm2 | 2Pair |  | TAS3-109-01 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CL010 GFHP Leak Detection - Level | 1.5mm2 | 2Pair |  | TAS3-106-01 | 42 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CL020 GFHP Leak Detection - Level | 1.5mm2 | 2Pair |  | TAS3-107-01 | 273 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CL030 GFHP Leak Detection - Level | 1.5mm2 | 2Pair |  | TAS3-206-01 | 430.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CL040 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CL040 GFHP Leak Detection - Level | 1.5mm2 | 2Pair |  | TAS3-207-01 | 514.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CP010 GFHP Pump Station Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-106-01 | 204.75 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020LFC20CT011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CT011 Geothermal Fluid Holding Pond - Temperature | 1.5mm2 | 1Triple |  | TAS3-201-01 | 204.75 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CT013 | P020CVA44 GFHP Pump RTD Junction Box | P020LFC20CT013 GFHP Pump A Stator 2 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CT014 | P020CVA44 GFHP Pump RTD Junction Box | P020LFC20CT014 GFHP Pump A Stator 3 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CT015 | P020CVA44 GFHP Pump RTD Junction Box | P020LFC20CT015 GFHP Pump A NDE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CT016 | P020CVA44 GFHP Pump RTD Junction Box | P020LFC20CT016 GFHP Pump A DE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CT022 | P020CVA45 GFHP Pump RTD Junction Box | P020LFC20CT022 GFHP Pump B Stator 1 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CT024 | P020CVA45 GFHP Pump RTD Junction Box | P020LFC20CT024 GFHP Pump B Stator 3 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CT026 | P020CVA45 GFHP Pump RTD Junction Box | P020LFC20CT026 GFHP Pump B DE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1132 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CY010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CY010 GFHP Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-02 | 204.75 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CY011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CY011 GFHP Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-02 | 204.75 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CY012 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CY012 GFHP Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-02 | 204.75 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CY020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CY020 GFHP Pump B - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-03 | 204.75 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CY021 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CY021 GFHP Pump B - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-03 | 204.75 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020LFC20CY022 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020LFC20CY022 GFHP Pump B - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-03 | 204.75 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NAB10AA030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10AA030 Condensate Pump A Outlet - MOV | 22AWG | 1Pair |  | TAS3-803-05 | 99.75 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
P020NAB10AA110 | P020NAB10AA030 Condensate Pump A Outlet - MOV | P020NAB10AA110 Condensate Pumps Bypass - MOV | 22AWG | 1Pair |  | TAS3-803-05 | 63 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
P020NAB10AP010_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10AP010_U01 Condensate Pump VSD | 1.0mm2 | 12C+E |  | TAS3-403-02 , TAS3-409-02 | 21 | C&I SGW | CS Cu - Tinned PVC / PVC
P020NAB10AP010_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10AP010_U01 Condensate Pump VSD | 1.5mm2 | 2Pair |  | TAS3-402-01 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NAB10AP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10AP010 Condensate Pump VSD | 980/1000μm | ABBTK811VO50 |  | TAS3-806-02 | 21 | C&I SGW | B TK811VO50 POF Cable Duplex Male Connectors
P020NAB10CF010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CF010 Condensate Pump Station Inlet - Flow | 2.5mm2 | 2C+E |  | TAS3-106-01 | 110 | C&I SGW | u - Tinned PVC / PVC
P020NAB10CF010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CF010 Condensate Pump Station Inlet - Flow | 1.5mm2 | 2Pair |  | TAS3-106-01 | 110 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NAB10CP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CP010 Inlet Filter - Pressure | 1.5mm2 | 2Pair |  | TAS3-106-01 | 94.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NAB10CP011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CP011 Condensate Pump A Inlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-106-01 | 94.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NAB10CP012 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CP012 Condensate Pump A Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-106-01 | 94.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NAB10CP030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CP030 Condensate Reinjection - Pressure | 1.5mm2 | 2Pair |  | TAS3-206-01 | 194.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NAB10CT012 | P020CVA47 Condensate Pump RTD Junction Box | P020NAB10CT012 Condensate Pump A Stator 1 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1142 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NAB10CT013 | P020CVA47 Condensate Pump RTD Junction Box | P020NAB10CT013 Condensate Pump A Stator 2 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1142 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NAB10CT014 | P020CVA47 Condensate Pump RTD Junction Box | P020NAB10CT014 Condensate Pump A Stator 3 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1142 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NAB10CT015 | P020CVA47 Condensate Pump RTD Junction Box | P020NAB10CT015 Condensate Pump A NDE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1142 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NAB10CT016 | P020CVA47 Condensate Pump RTD Junction Box | P020NAB10CT016 Condensate Pump A DE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1142 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NAB10CT030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CT030 Condensate Reinjection - Temperature | 1.5mm2 | 1Triple |  | TAS3-102-01 | 194.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NAB10CY010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CY010 Condensate Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-04 | 94.5 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NAB10CY011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CY011 Condensate Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-04 | 94.5 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NAB10CY012 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NAB10CY012 Condensate Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-04 | 94.5 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10AA110 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AA110 SGW Pump A Outlet - MOV | 22AWG | 1Pair |  | TAS3-803-04 | 99.75 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
P020NDB10AA120 | P020NDB10AA110 SGW Pump A Outlet - MOV | P020NDB10AA120 SGW Pump B Outlet - MOV | 22AWG | 1Pair |  | TAS3-803-04 | 21 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
P020NDB10AA130 | P020NDB10AA120 SGW Pump B Outlet - MOV | P020NDB10AA130 SGW Pump C Outlet - MOV | 22AWG | 1Pair |  | TAS3-803-04 | 21 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
P020NDB10AA140 | P020NDB10AA130 SGW Pump C Outlet - MOV | P020NDB10AA140 SGW Pumps Bypass - MOV | 22AWG | 1Pair |  | TAS3-803-04 | 21 | C&I SGW | ES Cu - Tinned PE/CPE (Grey Profibus)
P020NDB10AP010_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AP010_U01 SGW Pump A VSD | 1.0mm2 | 12C+E |  | TAS3-303-02 , TAS3-309-02 | 31.5 | C&I SGW | CS Cu - Tinned PVC / PVC
P020NDB10AP010_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AP010_U01 SGW Pump A VSD | 1.5mm2 | 2Pair |  | TAS3-302-01 | 31.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10AP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AP010 SGW Pump A VSD | 980/1000μm | ABBTK811VO50 |  | TAS3-806-01 | 31.5 | C&I SGW | B TK811VO50 POF Cable Duplex Male Connectors
P020NDB10AP020_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AP020_U01 SGW Pump B VSD | 1.0mm2 | 12C+E |  | TAS3-305-02 , TAS3-308-02 | 31.5 | C&I SGW | CS Cu - Tinned PVC / PVC
P020NDB10AP020_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AP020_U01 SGW Pump B VSD | 1.5mm2 | 2Pair |  | TAS3-302-01 | 31.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10AP020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AP020 SGW Pump B VSD | 980/1000μm | ABBTK811VO50 |  | TAS3-806-01 | 31.5 | C&I SGW | B TK811VO50 POF Cable Duplex Male Connectors
P020NDB10AP030_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AP030_U01 SGW Pump C VSD | 1.0mm2 | 12C+E |  | TAS3-403-02 , TAS3-409-02 | 31.5 | C&I SGW | CS Cu - Tinned PVC / PVC
P020NDB10AP030_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AP030_U01 SGW Pump C VSD | 1.5mm2 | 2Pair |  | TAS3-402-01 | 31.5 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10AP030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10AP030 SGW Pump C VSD | 980/1000μm | ABBTK811VO50 |  | TAS3-806-02 | 31.5 | C&I SGW | B TK811VO50 POF Cable Duplex Male Connectors
P020NDB10CF010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CF010 SGW Pump A Outlet - Flow | 1.5mm2 | 2Pair |  | TAS3-104-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CF020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CF020 SGW Pump B Outlet - Flow | 1.5mm2 | 2Pair |  | TAS3-206-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CF030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CF030 SGW Pump C Outlet - Flow | 1.5mm2 | 2Pair |  | TAS3-205-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CP011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CP011 SGW Pump A Inlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-104-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CP014 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CP014 SGW Pump A Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-204-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CP021 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CP021 SGW Pump B Inlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-105-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CP024 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CP024 SGW Pump B Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-206-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CP031 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CP031 SGW Pump C Inlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-109-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CP034 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CP034 SGW Pump C Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-205-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CP040 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CP040 SGW Pump Station Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-204-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020NDB10CT010 | P020CVA46 SGW Pump RTD Junction Box | P020NDB10CT010 SGW Pump A Inlet - Temperature | 1.5mm2 | 1Triple |  | TAS3-101-01 | 31.5 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT013 | P020CVA41 SGW Pump RTD Junction Box | P020NDB10CT013 SGW Pump A DE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT014 | P020CVA41 SGW Pump RTD Junction Box | P020NDB10CT014 SGW Pump A NDE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT015 | P020CVA41 SGW Pump RTD Junction Box | P020NDB10CT015 SGW Pump A Stator 1 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT016 | P020CVA41 SGW Pump RTD Junction Box | P020NDB10CT016 SGW Pump A Stator 2 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT017 | P020CVA41 SGW Pump RTD Junction Box | P020NDB10CT017 SGW Pump A Stator 3 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT020 | P020CVA46 SGW Pump RTD Junction Box | P020NDB10CT020 SGW Pump B Inlet - Temperature | 1.5mm2 | 1Triple |  | TAS3-103-01 | 21 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT023 | P020CVA43 SGW Pump RTD Junction Box | P020NDB10CT023 SGW Pump B DE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT024 | P020CVA43 SGW Pump RTD Junction Box | P020NDB10CT024 SGW Pump B NDE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT025 | P020CVA43 SGW Pump RTD Junction Box | P020NDB10CT025 SGW Pump B Stator - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT026 | P020CVA43 SGW Pump RTD Junction Box | P020NDB10CT026 SGW Pump B Stator 2 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT027 | P020CVA43 SGW Pump RTD Junction Box | P020NDB10CT027 SGW Pump B Stator 3 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT030 | P020CVA46 SGW Pump RTD Junction Box | P020NDB10CT030 SGW Pump C Inlet - Temperature | 1.5mm2 | 1Triple |  | TAS3-102-01 | 31.5 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT033 | P020CVA42 SGW Pump RTD Junction Box | P020NDB10CT033 SGW Pump C DE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT034 | P020CVA42 SGW Pump RTD Junction Box | P020NDB10CT034 SGW Pump C NDE Bearing - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT035 | P020CVA42 SGW Pump RTD Junction Box | P020NDB10CT035 SGW Pump C Stator - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT036 | P020CVA42 SGW Pump RTD Junction Box | P020NDB10CT036 SGW Pump C Stator 2 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CT037 | P020CVA42 SGW Pump RTD Junction Box | P020NDB10CT037 SGW Pump C Stator 3 - Temperature | 1.5mm2 | 1Triple |  | (*)ELE-SDG-1144 | 10 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY010 SGW Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-08 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY011 SGW Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-08 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY012 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY012 SGW Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-08 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY013 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY013 SGW Pump A - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-08 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY020 SGW Pump B - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-09 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY021 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY021 SGW Pump B - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-09 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY022 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY022 SGW Pump B - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-09 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY023 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY023 SGW Pump B - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-09 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY030 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY030 SGW Pump C - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-10 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY031 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY031 SGW Pump C - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-10 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY032 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY032 SGW Pump C - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-10 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020NDB10CY033 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020NDB10CY033 SGW Pump C - Vibration | 1.5mm2 | 1Triple |  | TAS3-820-10 | 84 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB20AA002_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AA002_Y01 Fin Fan Coolers Bypass - Solenoid | 2.5mm2 | 2C+E |  | TAS3-408-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020PCB20AA002 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AA002 Fin Fan Coolers Bypass - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-405-02 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020PCB20AA011_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AA011_Y01 Coolant Pump A Outlet CV - Solenoid | 2.5mm2 | 2C+E |  | TAS3-307-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020PCB20AA011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AA011 Coolant Pump A Outlet CV - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-306-02 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020PCB20AA021_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AA021_Y01 Coolant Pump B Outlet CV - Solenoid | 2.5mm2 | 2C+E |  | TAS3-407-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020PCB20AA021 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AA021 Coolant Pump B Outlet CV - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-406-02 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020PCB20AP010_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AP010_U01 SGW Pump VSD Cooling Circ Pump A VSD | 1.0mm2 | 12C+E |  | TAS3-305-02 , TAS3-309-02 | 21 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB20AP010_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AP010_U01 SGW Pump VSD Cooling Circ Pump A VSD | 1.5mm2 | 2Pair |  | TAS3-302-01 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB20AP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AP010 SGW Pump VSD Cooling Circ Pump A VSD | 980/1000μm | ABBTK811VO50 |  | TAS3-806-01 | 21 | C&I SGW | B TK811VO50 POF Cable Duplex Male Connectors
P020PCB20AP020_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AP020_U01 SGW Pump VSD Cooling Circ Pump B VSD | 1.0mm2 | 12C+E |  | TAS3-405-01 , TAS3-409-02 | 21 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB20AP020_U01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AP020_U01 SGW Pump VSD Cooling Circ Pump B VSD | 1.5mm2 | 2Pair |  | TAS3-402-01 | 21 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB20AP020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20AP020 SGW Pump VSD Cooling Circ Pump B VSD | 980/1000μm | ABBTK811VO50 |  | TAS3-806-02 | 21 | C&I SGW | B TK811VO50 POF Cable Duplex Male Connectors
P020PCB20CF010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CF010 Coolant Pump A Outlet - Flow | 2.5mm2 | 2C+E |  | TAS3-108-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020PCB20CF010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CF010 Coolant Pump A Outlet - Flow | 1.5mm2 | 2Pair |  | TAS3-108-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB20CF020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CF020 Coolant Pump B Outlet - Flow | 2.5mm2 | 2C+E |  | TAS3-208-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020PCB20CF020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CF020 Coolant Pump B Outlet - Flow | 1.5mm2 | 2Pair |  | TAS3-208-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB20CL010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CL010 Cooling Water Expansion Vessel - Level | 1.5mm2 | 2Pair |  | TAS3-108-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB20CP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CP010 Coolant Pumps Inlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-108-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB20CP040 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CP040 Coolant Pumps Outlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-208-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB20CT010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CT010 Fin Fan Coolers Cooling Water - Temperature | 1.5mm2 | 1Triple |  | TAS3-101-01 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB20CT011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CT011 Fin Fan Coolers Cooling Water - Temperature | 1.5mm2 | 1Triple |  | TAS3-202-01 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB20CT012 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB20CT012 Fin Fan Coolers Cooling Water - Temperature | 1.5mm2 | 1Triple |  | TAS3-203-01 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB22AA101 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB22AA101 SGW VSD A Cooling Water CV | 1.0mm2 | 4Pair |  | TAS3-301-01, TAS3-302-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB22AA102 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB22AA102 SGW VSD B Cooling Water CV | 1.0mm2 | 4Pair |  | TAS3-301-01, TAS3-302-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB22AA103 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB22AA103 SGW VSD C Cooling Water CV | 1.0mm2 | 4Pair |  | TAS3-401-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020PCB22CT011 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB22CT011 SGW VSD A Cooling Water - Temperature | 1.5mm2 | 1Triple |  | TAS3-103-01 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB22CT012 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB22CT012 SGW VSD B Cooling Water - Temperature | 1.5mm2 | 1Triple |  | TAS3-103-01 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB22CT013 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB22CT013 SGW VSD C Cooling Water - Temperature | 1.5mm2 | 1Triple |  | TAS3-202-01 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB22CT021 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB22CT021 SGW VSD A Cooling Water - Temperature | 1.5mm2 | 1Triple |  | TAS3-103-01 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB22CT022 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB22CT022 SGW VSD B Cooling Water - Temperature | 1.5mm2 | 1Triple |  | TAS3-103-01 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB22CT023 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB22CT023 SGW VSD C Cooling Water - Temperature | 1.5mm2 | 1Triple |  | TAS3-202-01 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020PCB23AA061_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB23AA061_Y01 SGW VSD CLG Water Bypass CV - Solenoid | 2.5mm2 | 2C+E |  | TAS3-408-01 | 47.25 | C&I SGW | u - Tinned PVC / PVC
P020PCB23AA061 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB23AA061 SGW VSD CLG Water Bypass CV - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-406-02 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020PCB31AA071_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB31AA071_Y01 Fin Fan Cooler A - Solenoid | 2.5mm2 | 2C+E |  | TAS3-307-01 | 73.5 | C&I SGW | u - Tinned PVC / PVC
P020PCB31AA071 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB31AA071 Fin Fan Cooler A - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-111-01 | 73.5 | C&I SGW | S Cu - Tinned PVC / PVC
P020PCB31AH010_M01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB31AH010_M01 VSD Cooling Fan Cooler A M01 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-01, TAS3-304-01, TAS3-305-01, TAS3-309-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB31AH010_M02 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB31AH010_M02 VSD Cooling Fan Cooler A M02 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-01, TAS3-304-01, TAS3-305-01, TAS3-309-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB31AH010_M03 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB31AH010_M03 VSD Cooling Fan Cooler A M03 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-01, TAS3-304-01, TAS3-305-01, TAS3-309-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB31AH010_M04 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB31AH010_M04 VSD Cooling Fan Cooler A M04 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-01, TAS3-304-01, TAS3-305-01, TAS3-309-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB32AA081_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB32AA081_Y01 Fin Fan Cooler B - Solenoid | 2.5mm2 | 2C+E |  | TAS3-308-01 | 73.5 | C&I SGW | u - Tinned PVC / PVC
P020PCB32AA081 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB32AA081 Fin Fan Cooler B - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-211-01 | 73.5 | C&I SGW | S Cu - Tinned PVC / PVC
P020PCB32AH020_M01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB32AH020_M01 VSD Cooling Fan Cooler B M01 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-01, TAS3-304-01, TAS3-305-01, TAS3-309-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB32AH020_M02 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB32AH020_M02 VSD Cooling Fan Cooler B M02 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-01, TAS3-304-01, TAS3-305-01, TAS3-309-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB32AH020_M03 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB32AH020_M03 VSD Cooling Fan Cooler B M03 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-01, TAS3-304-01, TAS3-305-01, TAS3-309-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB32AH020_M04 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB32AH020_M04 VSD Cooling Fan Cooler B M04 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-303-02, TAS3-304-02, TAS3-305-02, TAS3-309-02 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB33AA091_Y01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB33AA091_Y01 Fin Fan Cooler C - Solenoid | 2.5mm2 | 2C+E |  | TAS3-407-01 | 73.5 | C&I SGW | u - Tinned PVC / PVC
P020PCB33AA091 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB33AA091 Fin Fan Cooler C - Limit Switches | 1.0mm2 | 7C+E |  | TAS3-404-02 | 73.5 | C&I SGW | S Cu - Tinned PVC / PVC
P020PCB33AH030_M01 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB33AH030_M01 VSD Cooling Fan Cooler C M01 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-403-01, TAS3-404-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB33AH030_M02 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB33AH030_M02 VSD Cooling Fan Cooler C M02 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-403-01, TAS3-404-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB33AH030_M03 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB33AH030_M03 VSD Cooling Fan Cooler C M03 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-403-01, TAS3-404-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020PCB33AH030_M04 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020PCB33AH030_M04 VSD Cooling Fan Cooler C M04 - MCC Cell | 1.0mm2 | 12C+E |  | TAS3-403-01, TAS3-404-01 | 26.25 | C&I SGW | CS Cu - Tinned PVC / PVC
P020QFA11AN001 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020QFA11AN001 Compressor A | 1.0mm2 | 7C+E |  | TAS3-306-01 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020QFA12AN002 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020QFA12AN002 Compressor B | 1.0mm2 | 7C+E |  | TAS3-406-01 | 47.25 | C&I SGW | S Cu - Tinned PVC / PVC
P020QFB10CP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020QFB10CP010 Air Receiver A - Pressure | 1.5mm2 | 2Pair |  | TAS3-108-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020QFB10CP020 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020QFB10CP020 Air Receiver B - Pressure | 1.5mm2 | 2Pair |  | TAS3-109-01 | 47.25 | C&I SGW | ESCS Cu - Tinned PVC / PVC
P020SAA10CF195 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020SAA10CF195 Safety Shower - Unit 1 | 1.5mm2 | 1Triple |  | TAS3-605-02 | 47.25 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020SAA10CT001 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020SAA10CT001 Control Room Temperature | 1.5mm2 | 1Triple |  | TAS3-201-01 | 13 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020SAA10CT002 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020SAA10CT002 LV Switchroom Temperature | 1.5mm2 | 1Triple |  | TAS3-201-01 | 13 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020SAA10CT003 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020SAA10CT003 Battery Room Temperature | 1.5mm2 | 1Triple |  | TAS3-201-01 | 13 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020SAA10CT004 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020SAA10CT004 11kV Switchroom Temperature | 1.5mm2 | 1Triple |  | TAS3-201-01 | 13 | C&I SGW | le ES Cu - Tinned PVC / PVC
P020SAA10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020SAA10 HVAC System A | 1.0mm2 | 12C+E |  | TAS3-505-02 | 21 | C&I SGW | CS Cu - Tinned PVC / PVC
P020SAA10 | P020CRS10 Pump Station Server Cabinet HSW5 | P020SAA10 Building HVAC Services | 0.5mm2 | 4Pair |  | TAS3-805-01 | 26.25 | C&I SGW | Cu - CAT6 STP
P020SAB10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020SAB10 HVAC System B | 1.0mm2 | 12C+E |  | TAS3-605-02 | 21 | C&I SGW | CS Cu - Tinned PVC / PVC
P020SGY10 | P020CRA10 Pump Station PLC Cabinet - TAS3 | P020SGY10 Fire Alarm System | 1.0mm2 | 12C+E |  | TAS3-605-01 | 21 | C&I SGW | CS Cu - Tinned PVC / PVC
P020SGY10 | P020CRS10 Pump Station Server Cabinet HSW5 | P020SGY10 Fire Alarm Panel | 0.5mm2 | 4Pair |  | TAS3-805-01 | 26.25 | C&I SGW | Cu - CAT6 STP
S020GKA21CF195 | P020CRA10 Pump Station PLC Cabinet - TAS3 | S020GKA21CF195 SGW Battery Room Eye Wash Flow | 1.5mm2 | 1Triple |  | TAS3-605-02 | 58.8 | C&I SGW | le ES Cu - Tinned PVC / PVC
S020NDB10CP010 | P020CRA10 Pump Station PLC Cabinet - TAS3 | S020NDB10CP010 SGW Pump Station Inlet - Pressure | 1.5mm2 | 2Pair |  | TAS3-104-01 | 84 | C&I SGW | ESCS Cu - Tinned PVC / PVC
0110BTL10 | 0110CRA10 PLC Cabinet TH11 | 0110BTL10 TH11 110VDC System | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0110BTL10 | 0110CRA10 PLC Cabinet TH11 | 0110BTL10 TH11 110VDC System | 1.0mm2 | 4Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0110CRA10 | - Unison 33kV Line - ADSS Cable Joint Pit | 0110CRA10 PLC Cabinet TH11 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1805 TH11-1500-01 | 150 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0110CRA10 | - Unison 33kV Line - ADSS Cable Joint Pit | 0110CRA10 PLC Cabinet TH11 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1805 TH11-1500-01 | 150 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0110LFC10CL010 | 0110CRA10 PLC Cabinet TH11 | 0110LFC10CL010 TH11 Wellpad Pond Level | 1.5mm2 | 2Pair |  | TAS1-1503-01 | 57.75 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0110NAB10AA110 | 0110CRA10 PLC Cabinet TH11 | 0110NAB10AA110 TH11 Reinjection Well MOV | 22AWG | 1Pair |  | TH11-803-01 | 42 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0110NAB10CF010 | 0110CRA10 PLC Cabinet TH11 | 0110NAB10CF010 TH11 Reinjection Well Flow | 1.5mm2 | 2Pair |  | TAS1-1503-01 | 36.75 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0110NAB10CP010 | 0110CRA10 PLC Cabinet TH11 | 0110NAB10CP010 TH11 Reinjection Well Pressure | 1.5mm2 | 2Pair |  | TAS1-1503-01 | 47.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0110SAA10CT010 | 0110CRA10 PLC Cabinet TH11 | 0110SAA10CT010 TH11 Buidling Temp | 1.5mm2 | 2Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0110SAA10 | 0110CRA10 PLC Cabinet TH11 | 0110SAA10 TH11 H2S Scrubber | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0110SAA10SW1 | 0110CRA10 PLC Cabinet TH11 | 0110SAA10SW1 TH11 Building Door Switch | 1.0mm2 | 4C |  | TAS1-1503-01 | 9.975 | C&I Wellpads | Cu - Tinned PVC / PVC
0120BTL10 | 0120CRA10 PLC Cabinet TH12 | 0120BTL10 TH12 110VDC System | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0120BTL10 | 0120CRA10 PLC Cabinet TH12 | 0120BTL10 TH12 110VDC System | 1.0mm2 | 4Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0120CRA10 | - 11kV O/H Pole 25/1/1 - ADSS Cable Joint Pit | 0120CRA10 PLC Cabinet TH12 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1806 TH12-1500-01 | 168 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0120CRA10 | - 11kV O/H Pole 25/1/1 - ADSS Cable Joint Pit | 0120CRA10 PLC Cabinet TH12 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1806 TH12-1500-01 | 168 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0120LFC10CL010 | 0120CRA10 PLC Cabinet TH12 | 0120LFC10CL010 TH12 Wellpad Silencer Level | 1.5mm2 | 2Pair |  | TH12-1500-01 | 94.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0120LFC10CL020 | 0120CRA10 PLC Cabinet TH12 | 0120LFC10CL020 TH12 Wellpad Pond Level | 1.5mm2 | 2Pair |  | TH12-1500-01 | 68.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0120LFC10CP010 | 0120CRA10 PLC Cabinet TH12 | 0120LFC10CP010 TH12 Wellpad Silencer Pressure | 1.5mm2 | 2Pair |  | TH12-1500-01 | 94.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0120NDA10AA011 | 0120CRA10 PLC Cabinet TH12 | 0120NDA10AA011 TH12 Production Well MOV | 22AWG | 1Pair |  | TH12-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0120NDA10AA110 | 0120CRA10 PLC Cabinet TH12 | 0120NDA10AA110 TH12 Production Well MOV | 22AWG | 1Pair |  | TH12-803-01 | 63 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0120NDA10CF010 | 0120CRA10 PLC Cabinet TH12 | 0120NDA10CF010 TH12 Production Well Flow | 1.5mm2 | 2Pair |  | TH12-1500-01 | 63 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0120NDA10CP010 | 0120CRA10 PLC Cabinet TH12 | 0120NDA10CP010 TH12 Production Well Pressure | 1.5mm2 | 2Pair |  | TH12-1500-01 | 73.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0120NDA10CT010 | 0120CRA10 PLC Cabinet TH12 | 0120NDA10CT010 TH12 Production Well Temperature | 1.5mm2 | 2Pair |  | TH12-1500-01 | 63 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0120SAA10CT010 | 0120CRA10 PLC Cabinet TH12 | 0120SAA10CT010 TH12 Buidling Temp | 1.5mm2 | 2Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0120SAA10 | 0120CRA10 PLC Cabinet TH12 | 0120SAA10 TH12 H2S Scrubber | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0120SAA10SW1 | 0120CRA10 PLC Cabinet TH12 | 0120SAA10SW1 TH12 Building Door Switch | 1.0mm2 | 4C |  | TAS1-1503-01 | 9.975 | C&I Wellpads | Cu - Tinned PVC / PVC
0210NDA10AA011 | 0120CRA10 PLC Cabinet TH12 | 0210NDA10AA011 TH21 Production Well MOV | 22AWG | 1Pair |  | TH12-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0210NDA10AA110 | 0120CRA10 PLC Cabinet TH12 | 0210NDA10AA110 TH21 Production Well MOV | 22AWG | 1Pair |  | TH12-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0210NDA10CF010 | 0120CRA10 PLC Cabinet TH12 | 0210NDA10CF010 TH21 Production Well Flow | 1.5mm2 | 2Pair |  | TH12-1500-01 | 52.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0210NDA10CP010 | 0120CRA10 PLC Cabinet TH12 | 0210NDA10CP010 TH21 Production Well Pressure | 1.5mm2 | 2Pair |  | TH12-1500-01 | 63 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0210NDA10CT010 | 0120CRA10 PLC Cabinet TH12 | 0210NDA10CT010 TH21 Production Well Temperature | 1.5mm2 | 2Pair |  | TH12-1500-01 | 52.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0260BTL10 | 0260CRA10 PLC Cabinet TH26 | 0260BTL10 TH26 110VDC System | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0260BTL10 | 0260CRA10 PLC Cabinet TH26 | 0260BTL10 TH26 110VDC System | 1.0mm2 | 4Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0260CRA10 | - PLP26A | 0260CRA10 PLC Cabinet TH26 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1806 TH26-1500-01 | 955.5 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0260CRA10 | - PLP26B | 0260CRA10 PLC Cabinet TH26 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1806 TH26-1500-01 | 955.5 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0260LFC10CL010 | 0260CRA10 PLC Cabinet TH26 | 0260LFC10CL010 TH26 Wellpad Silencer Level | 1.5mm2 | 2Pair |  | TH26-1500-01 | 84 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0260LFC10CL020 | 0260CRA10 PLC Cabinet TH26 | 0260LFC10CL020 TH26 Wellpad Pond Level | 1.5mm2 | 2Pair |  | TH26-1500-01 | 78.75 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0260LFC10CP010 | 0260CRA10 PLC Cabinet TH26 | 0260LFC10CP010 TH26 Wellpad Silencer Pressure | 1.5mm2 | 2Pair |  | TH26-1500-01 | 84 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0260NDA10AA011 | 0260CRA10 PLC Cabinet TH26 | 0260NDA10AA011 TH26 Production Well MOV | 22AWG | 1Pair |  | TH26-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0260NDA10AA110 | 0260CRA10 PLC Cabinet TH26 | 0260NDA10AA110 TH26 Production Well MOV | 22AWG | 1Pair |  | TH26-803-01 | 63 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0260NDA10CF010 | 0260CRA10 PLC Cabinet TH26 | 0260NDA10CF010 TH26 Production Well Flow | 1.5mm2 | 2Pair |  | TH26-1500-01 | 73.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0260NDA10CP010 | 0260CRA10 PLC Cabinet TH26 | 0260NDA10CP010 TH26 Production Well Pressure | 1.5mm2 | 2Pair |  | TH26-1500-01 | 73.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0260NDA10CT010 | 0260CRA10 PLC Cabinet TH26 | 0260NDA10CT010 TH26 Production Well Temperature | 1.5mm2 | 2Pair |  | TH26-1500-01 | 63 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0260SAA10CT010 | 0260CRA10 PLC Cabinet TH26 | 0260SAA10CT010 TH26 Buidling Temp | 1.5mm2 | 2Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0260SAA10 | 0260CRA10 PLC Cabinet TH26 | 0260SAA10 TH26 H2S Scrubber | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0260SAA10SW1 | 0260CRA10 PLC Cabinet TH26 | 0260SAA10SW1 TH26 Building Door Switch | 1.0mm2 | 4C |  | TAS1-1503-01 | 9.975 | C&I Wellpads | Cu - Tinned PVC / PVC
0280BTL10 | 0280CRA10 PLC Cabinet TH28 | 0280BTL10 TH28 110VDC System | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0280BTL10 | 0280CRA10 PLC Cabinet TH28 | 0280BTL10 TH28 110VDC System | 1.0mm2 | 4Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0280CRA10 | - 11kV O/H Pole 41 - ADSS Cable Joint Pit | 0280CRA10 PLC Cabinet TH28 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1806 TH28-1500-01 | 115.5 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0280CRA10 | - 11kV O/H Pole 41 - ADSS Cable Joint Pit | 0280CRA10 PLC Cabinet TH28 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1806 TH28-1500-01 | 115.5 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0280LFC10CL010 | 0280CRA10 PLC Cabinet TH28 | 0280LFC10CL010 TH28 Wellpad Silencer Level | 1.5mm2 | 2Pair |  | TH28-1500-01 | 105 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0280LFC10CL020 | 0280CRA10 PLC Cabinet TH28 | 0280LFC10CL020 TH28 Wellpad Pond Level | 1.5mm2 | 2Pair |  | TH28-1500-01 | 63 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0280LFC10CP010 | 0280CRA10 PLC Cabinet TH28 | 0280LFC10CP010 TH28 Wellpad Silencer Pressure | 1.5mm2 | 2Pair |  | TH28-1500-01 | 105 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0280NDA10AA011 | 0280CRA10 PLC Cabinet TH28 | 0280NDA10AA011 TH28 Reinjection Well MOV | 22AWG | 1Pair |  | TH12-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0280NDA10AA110 | 0280CRA10 PLC Cabinet TH28 | 0280NDA10AA110 TH28 Reinjection Well MOV | 22AWG | 1Pair |  | TH12-803-01 | 63 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0280NDA10CF010 | 0280CRA10 PLC Cabinet TH28 | 0280NDA10CF010 TH28 Production Well Flow | 1.5mm2 | 2Pair |  | TH28-1500-01 | 52.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0280NDA10CP010 | 0280CRA10 PLC Cabinet TH28 | 0280NDA10CP010 TH28 Production Well Pressure | 1.5mm2 | 2Pair |  | TH28-1500-01 | 63 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0280NDA10CT010 | 0280CRA10 PLC Cabinet TH28 | 0280NDA10CT010 TH28 Production Well Temperature | 1.5mm2 | 2Pair |  | TH28-1500-01 | 57.75 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0280SAA10CT010 | 0280CRA10 PLC Cabinet TH28 | 0280SAA10CT010 TH28 Buidling Temp | 1.5mm2 | 2Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0280SAA10 | 0280CRA10 PLC Cabinet TH28 | 0280SAA10 TH28 H2S Scrubber | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0280SAA10SW1 | 0280CRA10 PLC Cabinet TH28 | 0280SAA10SW1 TH28 Building Door Switch | 1.0mm2 | 4C |  | TAS1-1503-01 | 9.975 | C&I Wellpads | Cu - Tinned PVC / PVC
0290BTL10 | 0290CRA10 PLC Cabinet TH29 | 0290BTL10 TH29 110VDC System | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0290BTL10 | 0290CRA10 PLC Cabinet TH29 | 0290BTL10 TH29 110VDC System | 1.0mm2 | 4Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0290CRA10 | - PLP29A | 0290CRA10 PLC Cabinet TH29 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1806 TH29-1500-01 | 178.5 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0290CRA10 | - PLP29B | 0290CRA10 PLC Cabinet TH29 | 9/125μm | 12Core |  | TABG-JEC-0-000-CCI-SDG-1806 TH29-1500-01 | 178.5 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
0290LFC10CL010 | 0290CRA10 PLC Cabinet TH29 | 0290LFC10CL010 TH29 Wellpad Pond Level | 1.5mm2 | 2Pair |  | TH29-1500-01 | 68.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0290NDB10AA012 | 0290CRA10 PLC Cabinet TH29 | 0290NDB10AA012 TH29 Reinjection Well Manual Valve Position | 1.5mm2 | 2Pair |  | TH29-1500-01 | 68.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0290NDB10AA110 | 0290CRA10 PLC Cabinet TH29 | 0290NDB10AA110 TH29 Reinjection Well MOV | 22AWG | 1Pair |  | TH29-803-01 | 63 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0290NDB10CF010 | 0290CRA10 PLC Cabinet TH29 | 0290NDB10CF010 TH29 Reinjection Well Flow | 1.5mm2 | 2Pair |  | TH29-1500-01 | 68.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0290NDB10CP010 | 0290CRA10 PLC Cabinet TH29 | 0290NDB10CP010 TH29 Reinjection Well Pressure | 1.5mm2 | 2Pair |  | TH29-1500-01 | 73.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0290SAA10CT010 | 0290CRA10 PLC Cabinet TH29 | 0290SAA10CT010 TH29 Buidling Temp | 1.5mm2 | 2Pair |  | TAS1-1503-01 | 9.975 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0290SAA10 | 0290CRA10 PLC Cabinet TH29 | 0290SAA10 TH29 H2S Scrubber | 1.0mm2 | 12C+E |  | TAS1-1503-01 | 9.975 | C&I Wellpads | CS Cu - Tinned PVC / PVC
0290SAA10SW1 | 0290CRA10 PLC Cabinet TH29 | 0290SAA10SW1 TH29 Building Door Switch | 1.0mm2 | 4C |  | TAS1-1503-01 | 9.975 | C&I Wellpads | Cu - Tinned PVC / PVC
0300NDA10AA011 | 0260CRA10 PLC Cabinet TH26 | 0300NDA10AA011 TH30 Production Well MOV | 22AWG | 1Pair |  | TH26-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0300NDA10AA110 | 0260CRA10 PLC Cabinet TH26 | 0300NDA10AA110 TH30 Production Well MOV | 22AWG | 1Pair |  | TH26-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0300NDA10CF010 | 0260CRA10 PLC Cabinet TH26 | 0300NDA10CF010 TH30 Production Well Flow | 1.5mm2 | 2Pair |  | TH26-1500-01 | 63 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0300NDA10CP010 | 0260CRA10 PLC Cabinet TH26 | 0300NDA10CP010 TH30 Production Well Pressure | 1.5mm2 | 2Pair |  | TH26-1500-01 | 63 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0300NDA10CT010 | 0260CRA10 PLC Cabinet TH26 | 0300NDA10CT010 TH30 Production Well Temperature | 1.5mm2 | 2Pair |  | TH26-1500-01 | 52.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0310NDB10AA012 | 0290CRA10 PLC Cabinet TH29 | 0310NDB10AA012 TH31 Reinjection Well Manual Valve Position | 1.5mm2 | 2Pair |  | TH29-1500-01 | 57.75 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0310NDB10AA110 | 0290NDB10AA110 TH29 Reinjection Well MOV | 0310NDB10AA110 TH31 Reinjection Well MOV | 22AWG | 1Pair |  | TH29-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0310NDB10CF010 | 0290CRA10 PLC Cabinet TH29 | 0310NDB10CF010 TH31 Reinjection Well Flow | 1.5mm2 | 2Pair |  | TH29-1500-01 | 57.75 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0310NDB10CP010 | 0290CRA10 PLC Cabinet TH29 | 0310NDB10CP010 TH31 Reinjection Well Pressure | 1.5mm2 | 2Pair |  | TH29-1500-01 | 63 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0340NDA10AA011 | 0280CRA10 PLC Cabinet TH28 | 0340NDA10AA011 TH34 Reinjection Well MOV | 22AWG | 1Pair |  | TH12-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0340NDA10AA110 | 0280CRA10 PLC Cabinet TH28 | 0340NDA10AA110 TH34 Reinjection Well MOV | 22AWG | 1Pair |  | TH12-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
0340NDA10CF010 | 0280CRA10 PLC Cabinet TH28 | 0340NDA10CF010 TH34 Production Well Flow | 1.5mm2 | 2Pair |  | TH28-1500-01 | 47.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0340NDA10CP010 | 0280CRA10 PLC Cabinet TH28 | 0340NDA10CP010 TH34 Production Well Pressure | 1.5mm2 | 2Pair |  | TH28-1500-01 | 52.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
0340NDA10CT010 | 0280CRA10 PLC Cabinet TH28 | 0340NDA10CT010 TH34 Production Well Temperature | 1.5mm2 | 2Pair |  | TH28-1500-01 | 47.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
EA30NDB10AA012 | 0290CRA10 PLC Cabinet TH29 | EA30NDB10AA012 TH35 Reinjection Well Manual Valve Position | 1.5mm2 | 2Pair |  | TH29-1500-01 | 47.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
EA30NDB10AA110 | 0310NDB10AA110 TH31 Reinjection Well MOV | EA30NDB10AA110 TH35 Reinjection Well MOV | 22AWG | 1Pair |  | TH29-803-01 | 19.95 | C&I Wellpads | ES Cu - Tinned PE/CPE (Grey Profibus)
EA30NDB10CF010 | 0290CRA10 PLC Cabinet TH29 | EA30NDB10CF010 TH35 Reinjection Well Flow | 1.5mm2 | 2Pair |  | TH29-1500-01 | 47.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
EA30NDB10CP010 | 0290CRA10 PLC Cabinet TH29 | EA30NDB10CP010 TH35 Reinjection Well Pressure | 1.5mm2 | 2Pair |  | TH29-1500-01 | 52.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
L050NDA10CT030 | 0120CRA10 PLC Cabinet TH12 | L050NDA10CT030 TH12 Wellpad Temperature | 1.5mm2 | 2Pair |  | TH12-1500-01 | 47.25 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
L060NDA10CT030 | 0280CRA10 PLC Cabinet TH28 | L060NDA10CT030 TH28 Wellpad Temperature | 1.5mm2 | 2Pair |  | TH28-1500-01 | 52.5 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
L070LFC10CL010 | 0280CRA10 PLC Cabinet TH28 | L070LFC10CL010 Local Pond Level | 1.5mm2 | 2Pair |  | TH28-1500-01 | 252 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
L070NDA10CT030 | 0260CRA10 PLC Cabinet TH26 | L070NDA10CT030 TH26 Wellpad Temperature | 1.5mm2 | 2Pair |  | TH26-1500-01 | 42 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
L190NDB10CP011 | 0290CRA10 PLC Cabinet TH29 | L190NDB10CP011 TH29 Wellpad SGW Reinjection Level | 1.5mm2 | 2Pair |  | TH29-1500-01 | 84 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
L190NDB10CT010 | 0290CRA10 PLC Cabinet TH29 | L190NDB10CT010 TH29 Wellpad SGW Reinjection Temperature | 1.5mm2 | 2Pair |  | TH29-1500-01 | 84 | C&I Wellpads | ESCS Cu - Tinned PVC / PVC
PLP26A | OLP42 11kV O/H Pole 42 - ADSS Cable Joint Pit | PLP26A Junction to TH26 (near Pole 42/7) Branch Pull Pit 1 | 9/125μm | 48Core |  | TABG-JEC-0-000-CCI-SDG-1806 TABG-JEC-0-000-ELE-RTD-0800 | 745.5 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
PLP26B | OLP42 11kV O/H Pole 42 - ADSS Cable Joint Pit | PLP26B Junction to TH26 (near Pole 42/7) Branch Pull Pit 2 | 9/125μm | 48Core |  | TABG-JEC-0-000-CCI-SDG-1806 TABG-JEC-0-000-ELE-RTD-0800 | 745.5 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
PLP29A | PLP26A Junction to TH26 (near Pole 42/7) Branch Pull Pit 1 | PLP29A Wellpad TH29 Pull Pit 1 | 9/125μm | 48Core |  | TABG-JEC-0-000-CCI-SDG-1806 TABG-JEC-0-000-ELE-RTD-0800 | 3990 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
PLP29B | PLP26B Junction to TH26 (near Pole 42/7) Branch Pull Pit 2 | PLP29B Wellpad TH29 Pull Pit 2 | 9/125μm | 48Core |  | TABG-JEC-0-000-CCI-SDG-1806 TABG-JEC-0-000-ELE-RTD-0800 | 3990 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
S020CRS20 | - 11kV O/H Ring Pole 3 - ADSS Cable Joint Pit | S020CRS20 Separation Plant Server Cabinet NSP | 9/125μm | 48Core |  | TABG-JEC-0-000-CCI-SDG-1806 TABG-JEC-0-000-ELE-PLN-2702 | 36.75 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
S020CRS20 | - 11kV O/H Ring Pole 3/1 - ADSS Cable Joint Pit | S020CRS20 Separation Plant Server Cabinet NSP | 9/125μm | 48Core |  | TABG-JEC-0-000-CCI-SDG-1806 TABG-JEC-0-000-ELE-PLN-2702 | 73.5 | C&I Wellpads | re Singlemode OS2 PE/GRP Armour/ PE / Polyamide Outdoor Jacket (Direct Burial Spec)
P1/1 | - Unison 11kV Switchgear | P1/1 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 110 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P1/1 | - Unison 11kV Switchgear | P1/1 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 110 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P1/1 | - Unison 11kV Switchgear | P1/1 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 110 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P1/1 | - Unison 11kV Switchgear | P1/1 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 110 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P1/1 | - Unison 11kV Switchgear | P1/1 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 110 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P1/1 | - Unison 11kV Switchgear | P1/1 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 110 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P32 | P33 11kV OHL POLE | P32 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 188 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P32 | P33 11kV OHL POLE | P32 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 188 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P32 | P33 11kV OHL POLE | P32 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 188 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P32 | P33 11kV OHL POLE | P32 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 188 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P32 | P33 11kV OHL POLE | P32 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 188 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P32 | P33 11kV OHL POLE | P32 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7004 | 188 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P42/6 | P42/7 11kV OHL POLE | P42/6 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7005 | 253 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P42/6 | P42/7 11kV OHL POLE | P42/6 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7005 | 253 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
P42/6 | P42/7 11kV OHL POLE | P42/6 11kV OHL POLE | 630mm2 | 1C |  | ELE-RTD-7005 | 253 | Power 11kV | XLPE/10KA/LSZH 6.35/11kV
L050NDA10AA030 | S020BFA10 SP 400V SWITCHBOARD | L050NDA10AA030 TH12 TO HP SEPARATOR MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 112 | Power Sep | XLPE/LSZH 0.6/1kV
L050NDA10AA040 | S020BFA10 SP 400V SWITCHBOARD | L050NDA10AA040 TH12 TO SILENCER MOV | 6mm2 | 3C+E |  | ELE-SLD-2312 | 112 | Power Sep | XLPE/LSZH 0.6/1kV
L060NDA10AA030 | S020BFA10 SP 400V SWITCHBOARD | L060NDA10AA030 TH28 TO HP SEPARATOR MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 112 | Power Sep | XLPE/LSZH 0.6/1kV
L060NDA10AA040 | S020BFA10 SP 400V SWITCHBOARD | L060NDA10AA040 TH28 TO SILENCER MOV | 6mm2 | 3C+E |  | ELE-SLD-2312 | 112 | Power Sep | XLPE/LSZH 0.6/1kV
L070NDA10AA030 | S020BFA10 SP 400V SWITCHBOARD | L070NDA10AA030 TH26 TO HP SEPARATOR MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 112 | Power Sep | XLPE/LSZH 0.6/1kV
L070NDA10AA040 | S020BFA10 SP 400V SWITCHBOARD | L070NDA10AA040 TH26 TO SILENCER MOV | 6mm2 | 3C+E |  | ELE-SLD-2312 | 112 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A | 4mm2 | 2C+E |  | ELE-SLD-2300 | 50 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A | 1.5mm2 | 12C+E |  | ELE-SLD-2300 | 50 | Power Sep | Cu PVC/PVC 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B | 4mm2 | 2C+E |  | ELE-SLD-2300 | 60 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B | 1.5mm2 | 12C+E |  | ELE-SLD-2300 | 60 | Power Sep | Cu PVC/PVC 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A N | 630mm2 | 1C |  | ELE-SLD-2300 | 50 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A N | 630mm2 | 1C |  | ELE-SLD-2300 | 50 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B N | 630mm2 | 1C |  | ELE-SLD-2300 | 60 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B N | 630mm2 | 1C |  | ELE-SLD-2300 | 60 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A L3 | 630mm2 | 1C |  | ELE-SLD-2300 | 50 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A L1 | 630mm2 | 1C |  | ELE-SLD-2300 | 50 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A L2 | 630mm2 | 1C |  | ELE-SLD-2300 | 50 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A L3 | 630mm2 | 1C |  | ELE-SLD-2300 | 50 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A L1 | 630mm2 | 1C |  | ELE-SLD-2300 | 50 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT010 SP Local Services Transformer 1 | S020BFA10 SEPARATION PLANT INCOMER A L2 | 630mm2 | 1C |  | ELE-SLD-2300 | 50 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFV10 Emergency Diesel Generator A Temporary JB | S020BFA10 SEPARATION PLANT EDG INCOMER A | 70mm2 | 4C+E |  | ELE-SLD-2300 | 42 | Power Sep | ex Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFV20 Emergency Diesel Generator B Temporary JB | S020BFA10 SEPARATION PLANT EDG INCOMER B | 70mm2 | 4C+E |  | ELE-SLD-2300 | 37 | Power Sep | ex Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BUA10 110VDC DISTRIBUTION A | S020BFA10 SP 400V SWITCHBOARD BUS A - 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-2330 | 39 | Power Sep | PE/LSZH 0.6/1kV
S020BFA10 | S020BUB10 110VDC DISTRIBUTION B | S020BFA10 SP 400V SWITCHBOARD BUS A - 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-2330 | 39 | Power Sep | PE/LSZH 0.6/1kV
S020BFA10 | S020BUA10 110VDC DISTRIBUTION A | S020BFA10 SP 400V SWITCHBOARD BUS B - 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-2330 | 39 | Power Sep | PE/LSZH 0.6/1kV
S020BFA10 | S020BUB10 110VDC DISTRIBUTION B | S020BFA10 SP 400V SWITCHBOARD BUS B - 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-2330 | 39 | Power Sep | PE/LSZH 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B L3 | 630mm2 | 1C |  | ELE-SLD-2300 | 60 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B L1 | 630mm2 | 1C |  | ELE-SLD-2300 | 60 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B L2 | 630mm2 | 1C |  | ELE-SLD-2300 | 60 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B L3 | 630mm2 | 1C |  | ELE-SLD-2300 | 60 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B L1 | 630mm2 | 1C |  | ELE-SLD-2300 | 60 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA10 | S020BFT10GT020 SP Local Services Transformer 2 | S020BFA10 SEPARATION PLANT INCOMER B L2 | 630mm2 | 1C |  | ELE-SLD-2300 | 60 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BFA20_F01 | S020BFA20 General Lighting and Power Panel A | S020BFA20_F01 Outdoor Plant Lighting Circuit Separation Plant Building | 4mm2 | 2C+E |  | ELE-SLD-2400 | 120 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA20_F02/1 | S020BFA20_F02 Outdoor Plant Lighting Circuit Separation Plant Station - 1st JB | S020BFA20_F02/1 Outdoor Plant Lighting Circuit Separation Plant | 6mm2 | 2C+E |  | ELE-SLD-2400 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA20_F02 | S020BFA20_F02 General Lighting and Power Panel A | S020BFA20_F02 Outdoor Plant Lighting Circuit Separation Plant Station - 1st JB | 10mm2 | 2C+E |  | ELE-SLD-2400 | 70 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA20_F03/1 | S020BFA20_F03 Outdoor Plant Lighting Circuit Separation Plant Station - 1st JB | S020BFA20_F03/1 Outdoor Plant Lighting Circuit Separation Plant Station | 6mm2 | 2C+E |  | ELE-SLD-2400 | 265 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA20_F03 | S020BFA20_F03 General Lighting and Power Panel A | S020BFA20_F03 Outdoor Plant Lighting Circuit Separation Plant Station - 1st JB | 10mm2 | 2C+E |  | ELE-SLD-2400 | 185 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA20_F04 | S020BFA20 General Lighting and Power Panel A | S020BFA20_F04 Outdoor Plant Lighting Circuit Separation Plant Station | 10mm2 | 2C+E |  | ELE-SLD-2400 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA20_F05 | S020BFA20 General Lighting and Power Panel A | S020BFA20_F05 Outdoor Plant Lighting Circuit Separation Plant Building - Emergency | 4mm2 | 2C+E |  | ELE-SLD-2400 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA20_F11 | S020BFA20 General Lighting and Power Panel A | S020BFA20_F11 Outdoor General Socket - 1Ph 16A | 25mm2 | 2C+E |  | ELE-SLD-2400 | 140 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA20_F13 | S020BFA20 General Lighting and Power Panel A | S020BFA20_F13 Outdoor General Socket - 3Ph 63A | 25mm2 | 4C+E |  | ELE-SLD-2400 | 60 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA20 | S020BFA10 SP 400V SWITCHBOARD | S020BFA20 General Lighting and Power Panel A | 70mm2 | 4C+E |  | ELE-SLD-2304, ELE-SLD-2400 | 31 | Power Sep | ex Cu XLPE/Rubber 0.6/1kV
S020BFA30_F01 | S020BFA30 General Lighting Bnd Power Panel B | S020BFA30_F01 Outdoor Plant Lighting Circuit Separation Plant Building | 4mm2 | 2C+E |  | ELE-SLD-2410 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA30_F02 | S020BFA30 General Lighting Bnd Power Panel B | S020BFA30_F02 Outdoor Plant Lighting Circuit Separation Plant Station | 10mm2 | 2C+E |  | ELE-SLD-2410 | 265 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA30_F03 | S020BFA30 General Lighting Bnd Power Panel B | S020BFA30_F03 Outdoor Plant Lighting Circuit Separation Plant Station | 10mm2 | 2C+E |  | ELE-SLD-2410 | 310 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA30_F04 | S020BFA30 General Lighting Bnd Power Panel B | S020BFA30_F04 Outdoor Plant Lighting Circuit Separation Plant Building - Emergency | 4mm2 | 2C+E |  | ELE-SLD-2410 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA30_F10 | S020BFA30 General Lighting Bnd Power Panel B | S020BFA30_F10 Outdoor General Socket - 1Ph 16A | 10mm2 | 2C+E |  | ELE-SLD-2410 | 75 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA30_F13 | S020BFA30 General Lighting Bnd Power Panel B | S020BFA30_F13 Outdoor General Socket - 3Ph 63A | 25mm2 | 4C+E |  | ELE-SLD-2410 | 50 | Power Sep | XLPE/LSZH 0.6/1kV
S020BFA30 | S020BFA10 SP 400V SWITCHBOARD | S020BFA30 General Lighting and Power Panel B | 70mm2 | 4C+E |  | ELE-SLD-2313, ELE-SLD-2410 | 20 | Power Sep | ex Cu XLPE/Rubber 0.6/1kV
S020BFA40 | S020BFA10 SP 400V SWITCHBOARD | S020BFA40 Process DB A | 70mm2 | 4C+E |  | ELE-SLD-2304, ELE-SLD-2350 | 32 | Power Sep | ex Cu XLPE/Rubber 0.6/1kV
S020BFA50 | S020BFA10 SP 400V SWITCHBOARD | S020BFA50 Process DB B | 70mm2 | 4C+E |  | ELE-SLD-2313, ELE-SLD-2360 | 32 | Power Sep | ex Cu XLPE/Rubber 0.6/1kV
S020BFT10GT010 | 11kV POLE 3/1 11kV OHL POLE | S020BFT10GT010 SP Local Services Transformer 1 | 120mm2 | 3C |  | ELE-PLN-2702 | 76 | Power Sep | XLPE/10KA/LSZH 6.35/11kV
S020BRA10 | S020BUA10 110VDC DISTRIBUTION A | S020BRA10 SP 110VDC/230VAC INVERTER A | 25mm2 | 2C+E |  | ELE-SLD-2330 | 16 | Power Sep | XLPE/LSZH 0.6/1kV
S020BRA10 | S020BFA10 SP 400V SWITCHBOARD | S020BRA10 UPS System A Bypass Supply | 6mm2 | 2C+E |  | ELE-SLD-2313 | 16 | Power Sep | XLPE/LSZH 0.6/1kV
S020BRB10 | S020BUB10 110VDC DISTRIBUTION B | S020BRB10 SP 110VDC/230VAC INVERTER B | 25mm2 | 2C+E |  | ELE-SLD-2330 | 16 | Power Sep | XLPE/LSZH 0.6/1kV
S020BRB10 | S020BFA10 SP 400V SWITCHBOARD | S020BRB10 UPS System B Bypass Supply | 6mm2 | 2C+E |  | ELE-PLN-2710 | 16 | Power Sep | XLPE/LSZH 0.6/1kV
S020BTA10GA001 | S020BTA10 110V DC BATTERY A | S020BTA10GA001 BATTERY A FUSE BOX | 240mm2 | 2C |  | ELE-SLD-2330 | 6 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BTB10GA001 | S020BTB10 110V DC BATTERY B | S020BTB10GA001 BATTERY B FUSE BOX | 240mm2 | 2C |  | ELE-SLD-2330 | 6 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BTL10 | S020BFA10 SP 400V SWITCHBOARD | S020BTL10 110VDC Power Supply System A Battery Charger | 10mm2 | 4C+E |  | ELE-SLD-2313 | 39 | Power Sep | XLPE/LSZH 0.6/1kV
S020BTL10 | S020BTA10GA001 BATTERY A FUSE BOX | S020BTL10 110VDC Power Supply System A Battery Charger | 240mm2 | 2C |  | ELE-SLD-2330 | 39 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BTL10 | S020BTL10 110VDC Power Supply System A Battery Charger | S020BTL10 110VDC Power Supply System B Battery Charger | 240mm2 | 2C |  | ELE-SLD-2330 | 6 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020BTM10 | S020BFA10 SP 400V SWITCHBOARD | S020BTM10 110VDC Power Supply System B Battery Charger | 10mm2 | 4C+E |  | ELE-PLN-2710 | 33 | Power Sep | XLPE/LSZH 0.6/1kV
S020BTM10 | S020BTA10GA001 BATTERY B FUSE BOX | S020BTM10 110VDC Power Supply System B Battery Charger | 240mm2 | 2C |  | ELE-SLD-2330 | 33 | Power Sep | x Cu XLPE/Rubber 0.6/1kV
S020CRA20 | S020BFA40 Process DB A | S020CRA20 PLC Cabinet General Power Supply | 4mm2 | 2C+E |  | ELE-SLD-2350 | 20 | Power Sep | XLPE/LSZH 0.6/1kV
S020CRA20 | S020BUA10 110VDC DISTRIBUTION A | S020CRA20 PLC CABINET TAS1- COMMS 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA20 | S020BUB10 110VDC DISTRIBUTION B | S020CRA20 PLC CABINET TAS1- COMMS 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BFA40 Process DB A | S020CRA30 PLC Cabinet General Power Supply | 4mm2 | 2C+E |  | ELE-SLD-2350 | 20 | Power Sep | XLPE/LSZH 0.6/1kV
S020CRA30 | S020BUA10 110VDC DISTRIBUTION A | S020CRA30 PLC CABINET - COMMS 110V A SUPPLY A | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUA10 110VDC DISTRIBUTION A | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY A - 1 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUA10 110VDC DISTRIBUTION A | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY A - 2 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUA10 110VDC DISTRIBUTION A | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY A - 3 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUA10 110VDC DISTRIBUTION A | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY A - 4 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUA10 110VDC DISTRIBUTION A | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY A - 5 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUA10 110VDC DISTRIBUTION A | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY A - 6 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUB10 110VDC DISTRIBUTION B | S020CRA30 PLC CABINET - COMMS 110V B SUPPLY B | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUB10 110VDC DISTRIBUTION B | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY B - 1 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUB10 110VDC DISTRIBUTION B | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY B - 2 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUB10 110VDC DISTRIBUTION B | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY B - 3 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUB10 110VDC DISTRIBUTION B | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY B - 4 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUB10 110VDC DISTRIBUTION B | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY B - 5 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRA30 | S020BUB10 110VDC DISTRIBUTION B | S020CRA30 PLC CABINET - IO CLUSTERS 110V SUPPLY B - 6 | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRJ40 | S020BUA10 110VDC DISTRIBUTION A | S020CRJ40 PLC CABINET TAS4- COMMS 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRJ40 | S020BUA10 110VDC DISTRIBUTION A | S020CRJ40 PLC CABINET TAS4- Cluster 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-2331 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRJ40 | S020BUB10 110VDC DISTRIBUTION B | S020CRJ40 PLC CABINET TAS4- COMMS 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-2330 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRJ40 | S020BUB10 110VDC DISTRIBUTION B | S020CRJ40 PLC CABINET TAS4-Cluster 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-2331 | 24 | Power Sep | PE/LSZH 0.6/1kV
S020CRS20 | S020BFA40 Process DB A | S020CRS20 Server Cabinet NSP General Power Supply | 4mm2 | 2C+E |  | ELE-SLD-2350 | 20 | Power Sep | XLPE/LSZH 0.6/1kV
S020CRS20 | S020BRC10 SP 230VAC UPS A DB | S020CRS20 CS SERVER SUPPLY A | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 16 | Power Sep | u XLPE/LSZH 0.6/1kV
S020CRS20 | S020BRD10 SP 230VAC UPS B DB | S020CRS20 CS SERVER SUPPLY B | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 16 | Power Sep | u XLPE/LSZH 0.6/1kV
S020CRS20 | S020BRC10 SP 230VAC UPS A DB | S020CRS20 OWS SUPPLY A | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 16 | Power Sep | u XLPE/LSZH 0.6/1kV
S020CRS20 | S020BRD10 SP 230VAC UPS B DB | S020CRS20 OWS SUPPLY B | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 16 | Power Sep | u XLPE/LSZH 0.6/1kV
S020CRS20 | S020BUA10 110VDC DISTRIBUTION A | S020CRS20 NETWORK CABINET - COMMS 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-2330 | 16 | Power Sep | PE/LSZH 0.6/1kV
S020CRS20 | S020BUB10 110VDC DISTRIBUTION B | S020CRS20 NETWORK CABINET - COMMS 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-2330 | 16 | Power Sep | PE/LSZH 0.6/1kV
S020CRS40 | S020BUA10 110VDC DISTRIBUTION A | S020CRS40 Building Services Ntework Panel 110VDC UPS SUPPLY A | 4mm2 | 2C |  | ELE-SLD-2330 | 16 | Power Sep | PE/LSZH 0.6/1kV
S020CRS40 | S020BRC10 SP 230VAC UPS A DB | S020CRS40 Building Services Ntework Panel 230VAC UPS SUPPLY A | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 34 | Power Sep | u XLPE/LSZH 0.6/1kV
S020CRS40 | S020BRD10 SP 230VAC UPS B DB | S020CRS40 Building Services Ntework Panel 230VAC UPS SUPPLY B | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 34 | Power Sep | u XLPE/LSZH 0.6/1kV
S020CRS40 | S020BFA40 Process DB A | S020CRS40 Building Services Ntework Panel Generap Power Supply | 4mm2 | 2C+E |  | ELE-SLD-2350 | 20 | Power Sep | XLPE/LSZH 0.6/1kV
S020CRS40 | S020BUB10 110VDC DISTRIBUTION B | S020CRS40 Building Services Ntework Panel 110VDC UPS SUPPLY B | 4mm2 | 2C |  | ELE-SLD-2330 | 16 | Power Sep | PE/LSZH 0.6/1kV
S020CRU10 | S020BRC10 SP 230VAC UPS A DB | S020CRU10 OWS KVM SUPPLY A | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 51 | Power Sep | u XLPE/LSZH 0.6/1kV
S020CRU10 | S020BRD10 SP 230VAC UPS B DB | S020CRU10 OWS KVM SUPPLY B | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 51 | Power Sep | u XLPE/LSZH 0.6/1kV
S020CYU10 | S020BRC10 SP 230VAC UPS A DB | S020CYU10 Security System - Supply A | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 34 | Power Sep | u XLPE/LSZH 0.6/1kV
S020CYU10 | S020BRC10 SP 230VAC UPS A DB | S020CYU10 Security System - Supply B | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 34 | Power Sep | u XLPE/LSZH 0.6/1kV
S020GAC10AA021 | S020BFA10 SP 400V SWITCHBOARD | S020GAC10AA021 RAW WATER SUPPLY MOV | 4mm2 | 3C+E |  | ELE-SLD-2302 | 80 | Power Sep | XLPE/LSZH 0.6/1kV
S020GAC10AA031 | S020BFA10 SP 400V SWITCHBOARD | S020GAC10AA031 RAW WATER SUPPLY MOV | 4mm2 | 3C+E |  | ELE-SLD-2313 | 80 | Power Sep | XLPE/LSZH 0.6/1kV
S020GAC20AP010_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020GAC20AP010_-M01 Raw Water Pump A | 6mm2 | 3C+E |  | ELE-SLD-2301 | 40 | Power Sep | XLPE/LSZH 0.6/1kV
S020GAC20AP020_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020GAC20AP020_-M01 Raw Water Pump B | 6mm2 | 3C+E |  | ELE-SLD-2310 | 40 | Power Sep | XLPE/LSZH 0.6/1kV
S020GBK10AP010_-E01 | S020BFA10 SP 400V SWITCHBOARD | S020GBK10AP010_-E01 Calcite Inhibitor Load Out Pump Motor Control E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-2301 | 50 | Power Sep | u PVC/PVC 0.6/1kV
S020GBK10AP010 | S020BFA10 SP 400V SWITCHBOARD | S020GBK10AP010 Calcite Inhibitor Load Out Pump | 4mm2 | 3C+E |  | ELE-SLD-2301 | 50 | Power Sep | XLPE/LSZH 0.6/1kV
S020GBK10AP020 | S020BFA10 SP 400V SWITCHBOARD | S020GBK10AP020 Calcite Inhibitor Sump Pump | 4mm2 | 3C+E |  | ELE-SLD-2310 | 60 | Power Sep | XLPE/LSZH 0.6/1kV
S020GBK10 | S020BFA10 SP 400V SWITCHBOARD | S020GBK10 Calcite Inhibition Pumping System Package | 25mm2 | 4C+E |  | ELE-SLD-2302 | 50 | Power Sep | XLPE/LSZH 0.6/1kV
S020GKA10AP010_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020GKA10AP010_-M01 Potable Water Supply Pump A Motor | 6mm2 | 3C+E |  | ELE-SLD-2301 | 40 | Power Sep | XLPE/LSZH 0.6/1kV
S020GKA10AP020_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020GKA10AP020_-M01 Potable Water Supply Pump B Motor | 6mm2 | 3C+E |  | ELE-SLD-2310 | 40 | Power Sep | XLPE/LSZH 0.6/1kV
S020GKA20BB030_-H01 | S020BFA40 Process DB A | S020GKA20BB030_-H01 Emerg Shower Hot Water Cylinder Heater Acid Dosing | 10mm2 | 4C+E |  | ELE-SLD-2350 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020GKA20BB031_-H01 | S020BFA50 Process DB B | S020GKA20BB031_-H01 Emerg Shower Hot Water Cylinder Heater Acid Dosing | 10mm2 | 4C+E |  | ELE-SLD-2360 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020GKA20BB032_-H01 | S020BFA50 Process DB B | S020GKA20BB032_-H01 Emerg Shower Hot Water Cylinder Heater Acid Dosing | 10mm2 | 4C+E |  | ELE-SLD-2360 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020GKA20BB040_-H01 | S020BFA40 Process DB A | S020GKA20BB040_-H01 Emerg Shower Hot Water Cylinder Heater Separation Station | 10mm2 | 4C+E |  | ELE-SLD-2350 | 30 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA10AA001 | S020BFA10 SP 400V SWITCHBOARD | S020NAA10AA001 HP STEAM SCRUBBING LINE MOV | 25mm2 | 3C+E |  | ELE-SLD-2302 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA10AA002 | S020BFA10 SP 400V SWITCHBOARD | S020NAA10AA002 HP STEAM SCRUBBING LINE MOV | 25mm2 | 3C+E |  | ELE-SLD-2312 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA10AA140 | S020BFA10 SP 400V SWITCHBOARD | S020NAA10AA140 HP SCRUBBER LCV | 4mm2 | 3C+E |  | ELE-SLD-2311 | 120 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA11AA110 | S020BFA10 SP 400V SWITCHBOARD | S020NAA11AA110 HP CDPS LCV | 4mm2 | 3C+E |  | ELE-SLD-2311 | 120 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA20AA001 | S020BFA10 SP 400V SWITCHBOARD | S020NAA20AA001 IP STEAM SCRUBBING LINE MOV | 25mm2 | 3C+E |  | ELE-SLD-2302 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA20AA002 | S020BFA10 SP 400V SWITCHBOARD | S020NAA20AA002 IP STEAM SCRUBBING LINE MOV | 25mm2 | 3C+E |  | ELE-SLD-2312 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA31AA001 | S020BFA10 SP 400V SWITCHBOARD | S020NAA31AA001 LP STEAM SCRUBBING LINE A MOV | 25mm2 | 3C+E |  | ELE-SLD-2304 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA31AA002 | S020BFA10 SP 400V SWITCHBOARD | S020NAA31AA002 LP STEAM SCRUBBING LINE A MOV | 25mm2 | 3C+E |  | ELE-SLD-2312 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA31AA006 | S020BFA10 SP 400V SWITCHBOARD | S020NAA31AA006 LP SCRUBBING LINE BYPASS MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 72 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA31AA007 | S020BFA10 SP 400V SWITCHBOARD | S020NAA31AA007 LP SCRUBBING LINE BYPASS MOV | 6mm2 | 3C+E |  | ELE-SLD-2313 | 72 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA31AA503 | S020BFA10 SP 400V SWITCHBOARD | S020NAA31AA503 LP STEAM SCRUBBING LINE A MOV | 10mm2 | 3C+E |  | ELE-SLD-2302 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA31AA504 | S020BFA10 SP 400V SWITCHBOARD | S020NAA31AA504 LP STEAM SCRUBBING LINE A MOV | 10mm2 | 3C+E |  | ELE-SLD-2312 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA32AA001 | S020BFA10 SP 400V SWITCHBOARD | S020NAA32AA001 LP STEAM SCRUBBING LINE B MOV | 25mm2 | 3C+E |  | ELE-SLD-2304 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA32AA002 | S020BFA10 SP 400V SWITCHBOARD | S020NAA32AA002 LP STEAM SCRUBBING LINE B MOV | 25mm2 | 3C+E |  | ELE-SLD-2312 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA32AA503 | S020BFA10 SP 400V SWITCHBOARD | S020NAA32AA503 LP STEAM SCRUBBING LINE B MOV | 10mm2 | 3C+E |  | ELE-SLD-2302 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NAA32AA504 | S020BFA10 SP 400V SWITCHBOARD | S020NAA32AA504 LP STEAM SCRUBBING LINE B MOV | 10mm2 | 3C+E |  | ELE-SLD-2312 | 460 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA001 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA001 HP SEPARATOR OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 149 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA002 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA002 HP SEPARATOR OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 149 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA013 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA013 HP LCV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 143 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA023 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA023 HP LCV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 143 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA033 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA033 HP LCV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 143 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA041 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA041 HP EDV INLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA043 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA043 HP EDV INLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA051 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA051 HP EDV INLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA053 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA053 HP EDV INLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA061 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA061 HP EDV INLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA063 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA063 HP EDV INLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA071 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA071 HP MDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 149 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA072 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA072 HP MDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 149 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA073 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA073 HP MDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 149 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA20AA074 | S020BFA10 SP 400V SWITCHBOARD | S020NDA20AA074 HP MDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 149 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA21AH010_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020NDA21AH010_-M01 SGW Cooler for Acid Dilution (Air fan cooler) A | 6mm2 | 3C+E |  | ELE-SLD-2301 | 120 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA21AP010_-E01 | S020BFA10 SP 400V SWITCHBOARD | S020NDA21AP010_-E01 Acid Dilution SGW Pump A Motor Control E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-2301 | 120 | Power Sep | u PVC/PVC 0.6/1kV
S020NDA21AP010_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020NDA21AP010_-M01 Acid Dilution SGW Pump A Motor | 6mm2 | 3C+E |  | ELE-SLD-2301 | 120 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA22AH020_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020NDA22AH020_-M01 SGW Cooler for Acid Dilution (Air fan cooler) B | 6mm2 | 3C+E |  | ELE-SLD-2310 | 120 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA22AP020_-E01 | S020BFA10 SP 400V SWITCHBOARD | S020NDA22AP020_-E01 Acid Dilution SGW Pump B Motor Control E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-2310 | 120 | Power Sep | u PVC/PVC 0.6/1kV
S020NDA22AP020_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020NDA22AP020_-M01 Acid Dilution SGW Pump B Motor | 6mm2 | 3C+E |  | ELE-SLD-2310 | 120 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA23CQ010 | S020BRC10 SP 230VAC UPS A DB | S020NDA23CQ010 ANALYSER TRANSMITTER A (PH) HP SGW Drum Outlet pH Transmitter 10 | 4mm2 | 2C+E |  | ELE-SLD-2340 | 130 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA001 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA001 IP SEPARATOR OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 57 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA010 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA010 LP SEPARATOR A OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2312 | 114 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA011 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA011 LP SEPARATOR A OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 114 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA013 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA013 IP LCV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 83 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA020 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA020 LP SEPARATOR B OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2312 | 106 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA021 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA021 LP SEPARATOR B OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 106 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA023 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA023 IP LCV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 83 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA033 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA033 IP LCV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 83 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA043 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA043 IP LCV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 83 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA053 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA053 IP MDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 80 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA054 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA054 IP MDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2313 | 90 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA063 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA063 IP EDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2311 | 80 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA073 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA073 IP EDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 80 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA083 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA083 IP EDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2312 | 80 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDA30AA093 | S020BFA10 SP 400V SWITCHBOARD | S020NDA30AA093 IP EDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 80 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB10AA001 | S020BFA10 SP 400V SWITCHBOARD | S020NDB10AA001 LP SEPARATOR OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2312 | 143 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB10AA013 | S020BFA10 SP 400V SWITCHBOARD | S020NDB10AA013 LP EDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2312 | 138 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB10AA023 | S020BFA10 SP 400V SWITCHBOARD | S020NDB10AA023 LP EDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 138 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB10AA033 | S020BFA10 SP 400V SWITCHBOARD | S020NDB10AA033 LP EDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2312 | 138 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB10AA043 | S020BFA10 SP 400V SWITCHBOARD | S020NDB10AA043 LP EDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2302 | 138 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB10AA053 | S020BFA10 SP 400V SWITCHBOARD | S020NDB10AA053 LP MDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2303 | 138 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB10AA054 | S020BFA10 SP 400V SWITCHBOARD | S020NDB10AA054 LP MDV OUTLET MOV | 6mm2 | 3C+E |  | ELE-SLD-2313 | 138 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB11CQ010 | S020BRC10 SP 230VAC UPS A DB | S020NDB11CQ010 ANALYSER TRANSMITTER (PH) LP SGW Drum Outlet pH Transmitter 10 | 4mm2 | 2C+E |  | ELE-SLD-2340 | 130 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB12CQ010 | S020BRD10 SP 230VAC UPS B DB | S020NDB12CQ010 ANALYSER TRANSMITTER B (PH) LP SGW Drum Outlet pH Transmitter 010 | 4mm2 | 2C+E |  | ELE-SLD-2340 | 130 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB12CQ020 | S020BRD10 SP 230VAC UPS B DB | S020NDB12CQ020 ANALYSER TRANSMITTER B (PH) LP SGW Drum Outlet pH Transmitter 20 | 4mm2 | 2C+E |  | ELE-SLD-2340 | 130 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB13CQ020 | S020BRC10 SP 230VAC UPS A DB | S020NDB13CQ020 ANALYSER TRANSMITTER B (PH) LP SGW Drum Outlet pH Transmitter 20 | 4mm2 | 2C+E |  | ELE-SLD-2340 | 130 | Power Sep | XLPE/LSZH 0.6/1kV
S020NDB24CQ020 | S020BRC10 SP 230VAC UPS A DB | S020NDB24CQ020 ANALYSER TRANSMITTER (PH) HP SGW Drum Outlet pH Transmitter 20 | 4mm2 | 2C+E |  | ELE-SLD-2340 | 130 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM10CL020 | S020BRC10 SP 230VAC UPS A DB | S020QCM10CL020 Sulphuric Acid Tank Level Instrumentation. | 4mm2 | 2C+E |  | ELE-SLD-2340 | 130 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM10GU010_-C01 | S020BFA40 Process DB A | S020QCM10GU010_-C01 Acid dosing Heat Tracing Circuit 1 | 4mm2 | 2C+E |  | ELE-SLD-2350 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM10GU010_-C02 | S020BFA40 Process DB A | S020QCM10GU010_-C02 Acid dosing Heat Tracing Circuit 2 | 4mm2 | 2C+E |  | ELE-SLD-2350 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM10GU010_-C03 | S020BFA40 Process DB A | S020QCM10GU010_-C03 Acid dosing Heat Tracing Circuit 3 | 4mm2 | 2C+E |  | ELE-SLD-2350 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM10GU020_-C01 | S020BFA40 Process DB B | S020QCM10GU020_-C01 Acid dosing Heat Tracing Circuit 4 | 4mm2 | 2C+E |  | ELE-SLD-2360 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM10GU020_-C02 | S020BFA40 Process DB B | S020QCM10GU020_-C02 Acid dosing Heat Tracing Circuit 5 | 4mm2 | 2C+E |  | ELE-SLD-2360 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM10GU020_-C03 | S020BFA40 Process DB B | S020QCM10GU020_-C03 Acid dosing Heat Tracing Circuit 6 | 4mm2 | 2C+E |  | ELE-SLD-2360 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM20AP010_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020QCM20AP010_-M01 Acid Dosing Pump A Motor | 6mm2 | 3C+3E |  | ELE-SLD-2301 | 120 | Power Sep | ex Cu XLPE/EMC/Rubber 0.6/1kV
S020QCM20BB010_-C01 | S020BFA40 Process DB A | S020QCM20BB010_-C01 Sulphuric Acid Tank Heater - Blanket Heater 1 | 25mm2 | 2C+E |  | ELE-SLD-2350 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM20BB010_-C02 | S020BFA40 Process DB A | S020QCM20BB010_-C02 Sulphuric Acid Tank Heater - Blanket Heater 2 | 25mm2 | 2C+E |  | ELE-SLD-2350 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM20BB010_-C03 | S020BFA50 Process DB B | S020QCM20BB010_-C03 Sulphuric Acid Tank Heater - Blanket Heater 3 | 25mm2 | 2C+E |  | ELE-SLD-2360 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM20BB010_-C04 | S020BFA50 Process DB B | S020QCM20BB010_-C04 Sulphuric Acid Tank Heater - Blanket Heater 4 | 25mm2 | 2C+E |  | ELE-SLD-2360 | 150 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM21AP020_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020QCM21AP020_-M01 Acid Dosing Pump B Motor | 6mm2 | 3C+3E |  | ELE-SLD-2310 | 120 | Power Sep | ex Cu XLPE/EMC/Rubber 0.6/1kV
S020QCM30AP001_-M01 | S020BFA10 SP 400V SWITCHBOARD | S020QCM30AP001_-M01 Acid Dosing System Sump Pump Motor | 6mm2 | 3C+E |  | ELE-SLD-2301 | 120 | Power Sep | XLPE/LSZH 0.6/1kV
S020QCM30CQ010 | S020BRC10 SP 230VAC UPS A DB | S020QCM30CQ010 ANALYSER TRANSMITTER A (PH) 1 - Sulphuric Acid Dosing System Sump Pump pH Transmitter | 4mm2 | 2C+E |  | ELE-SLD-2340 | 130 | Power Sep | XLPE/LSZH 0.6/1kV
S020SAA10 | S020BFA10 SP 400V SWITCHBOARD | S020SAA10 Building HVAC A | 120mm2 | 4C+E |  | ELE-SLD-2313 | 27 | Power Sep | lex Cu XLPE/Rubber 0.6/1kV
S020SAB10 | S020BFA10 SP 400V SWITCHBOARD | S020SAB10 Building HVAC B | 120mm2 | 4C+E |  | ELE-PLN-2710 | 29 | Power Sep | lex Cu XLPE/Rubber 0.6/1kV
S020SGY10 | S020BRC10 SP 230VAC UPS A DB | S020SGY10 Fire Alarm System - Supply A | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 16 | Power Sep | u XLPE/LSZH 0.6/1kV
S020SGY10 | S020BRC10 SP 230VAC UPS B DB | S020SGY10 Fire Alarm System - Supply B | 2.5mm2 | 2C+E |  | ELE-SLD-2340 | 16 | Power Sep | u XLPE/LSZH 0.6/1kV
SPMEB | S020BFT10GT010 SP Local Services Transformer 1 | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 50 | Power Sep | PVC EARTH
SPMEB | S020BFT10GT010 SP Local Services Transformer 1 | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 50 | Power Sep | PVC EARTH
SPMEB | S020BFT10GT010 SP Local Services Transformer 1 | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 50 | Power Sep | PVC EARTH
SPMEB | S020BFT10GT020 SP Local Services Transformer 2 | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 50 | Power Sep | PVC EARTH
SPMEB | S020BFT10GT020 SP Local Services Transformer 2 | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 50 | Power Sep | PVC EARTH
SPMEB | S020BFT10GT020 SP Local Services Transformer 2 | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 50 | Power Sep | PVC EARTH
SPMEB | S020BFA10 SP 400V SWITCHBOARD | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 30 | Power Sep | PVC EARTH
SPMEB | S020BFA10 SP 400V SWITCHBOARD | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 30 | Power Sep | PVC EARTH
SPMEB | Roof Beam 1 BUILDING STRUCTURAL COLUMN | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 30 | Power Sep | PVC EARTH
SPMEB | Roof Beam 5 BUILDING STRUCTURAL COLUMN | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 30 | Power Sep | PVC EARTH
SPMEB | Roof Beam 6 BUILDING STRUCTURAL COLUMN | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 30 | Power Sep | PVC EARTH
SPMEB | Roof Beam 7 BUILDING STRUCTURAL COLUMN | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 30 | Power Sep | PVC EARTH
SPMEB | Wricon Building Structure Wricon | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 30 | Power Sep | PVC EARTH
SPMEB | Wricon Building Structure Wricon | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0330 | 30 | Power Sep | PVC EARTH
SPMEB | S020BTL10 110DC Charger A | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 35 | Power Sep | VC EARTH
SPMEB | S020BTL10 110DC Battery A | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 35 | Power Sep | VC EARTH
SPMEB | S020BTL10 110DC Charger B | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 35 | Power Sep | VC EARTH
SPMEB | S020BTL10 110DC Battery B | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 35 | Power Sep | VC EARTH
SPMEB | S020BRA10 UPS A | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 35 | Power Sep | VC EARTH
SPMEB | S020BRA10 UPS B | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 35 | Power Sep | VC EARTH
SPMEB | S020CRS10 NETWORK RACK A | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 40 | Power Sep | VC EARTH
SPMEB | S020CRA10 CONTROL SYSTEM | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 40 | Power Sep | VC EARTH
SPMEB | S020CRA10 CONTROL SYSTEM | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 40 | Power Sep | VC EARTH
SPMEB | - HPU LV Cable Ladder | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 60 | Power Sep | VC EARTH
SPMEB | - SP Plant Cable Ladder | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 250 | Power Sep | VC EARTH
SPMEB | - SP Plant Cable Ladder | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 250 | Power Sep | VC EARTH
SPMEB | - SP building Cable Ladder | SPMEB SP BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0331 | 60 | Power Sep | VC EARTH
SPMEB | SP EARTH GRADIENT | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0331 | 50 | Power Sep | PVC EARTH
SPMEB | SP EARTH GRADIENT | SPMEB SP BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0331 | 50 | Power Sep | PVC EARTH
L190NDB10AA001 | P020BFA10 SGW 400V SWITCHBOARD | L190NDB10AA001 SGW Crosscountry Line A ISO Valve | 6mm2 | 3C+E |  | ELE-SLD-1302 | 90 | Power SGW | XLPE/LSZH 0.6/1kV
L190NDB10AA002 | P020BFA10 SGW 400V SWITCHBOARD | L190NDB10AA002 SGW Crosscountry Line A ISO Valve | 6mm2 | 3C+E |  | ELE-SLD-1302 | 90 | Power SGW | XLPE/LSZH 0.6/1kV
L200NDB10AA001 | P020BFA10 SGW 400V SWITCHBOARD | L200NDB10AA001 SGW Crosscountry Line B ISO Valve | 6mm2 | 3C+E |  | ELE-SLD-1311 | 90 | Power SGW | XLPE/LSZH 0.6/1kV
L200NDB10AA002 | P020BFA10 SGW 400V SWITCHBOARD | L200NDB10AA002 SGW Crosscountry Line B ISO Valve | 6mm2 | 3C+E |  | ELE-SLD-1311 | 90 | Power SGW | XLPE/LSZH 0.6/1kV
P020BBA10GS020 | 11kV POLE 54/1 11kV OHL POLE | P020BBA10 11kV SWITCHGEAR INCOMER BUS A | 630mm2 | 1C |  | AKA-ELE-SLD-1000 | 475 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BBA10GS020 | 11kV POLE 54/1 11kV OHL POLE | P020BBA10 11kV SWITCHGEAR INCOMER BUS A | 630mm2 | 1C |  | AKA-ELE-SLD-1000 | 475 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BBA10GS020 | 11kV POLE 54/1 11kV OHL POLE | P020BBA10 11kV SWITCHGEAR INCOMER BUS A | 630mm2 | 1C |  | AKA-ELE-SLD-1000 | 475 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BBA10GS030 | 11kV POLE 3/3/1 11kV OHL POLE | P020BBA10 11kV SWITCHGEAR INCOMER BUS A (UNISON) | 630mm2 | 1C |  | AKA-ELE-SLD-1000 | 450 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BBA10GS030 | 11kV POLE 3/3/1 11kV OHL POLE | P020BBA10 11kV SWITCHGEAR INCOMER BUS A (UNISON) | 630mm2 | 1C |  | AKA-ELE-SLD-1000 | 450 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BBA10GS030 | 11kV POLE 3/3/1 11kV OHL POLE | P020BBA10 11kV SWITCHGEAR INCOMER BUS A (UNISON) | 630mm2 | 1C |  | AKA-ELE-SLD-1000 | 450 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BBA10GS030 | 11kV POLE 3/3/1 11kV OHL POLE | P020BBA10 11kV SWITCHGEAR INCOMER BUS A (UNISON) | 630mm2 | 1C |  | AKA-ELE-SLD-1000 | 450 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BBA10GS030 | 11kV POLE 3/3/1 11kV OHL POLE | P020BBA10 11kV SWITCHGEAR INCOMER BUS A (UNISON) | 630mm2 | 1C |  | AKA-ELE-SLD-1000 | 450 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BBA10GS030 | 11kV POLE 3/3/1 11kV OHL POLE | P020BBA10 11kV SWITCHGEAR INCOMER BUS A (UNISON) | 630mm2 | 1C |  | AKA-ELE-SLD-1000 | 450 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BBA10 | P02BFA40 Process DB A | P020BBA10 SGW 11kV Switchboard A & load Space Heater | 6mm2 | 4C+E |  | ELE-SLD-1350 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
P020BBA10 | P02BFA50 Process DB B | P020BBA10 SGW 11kV Switchboard B & load Space Heater | 6mm2 | 4C+E |  | ELE-SLD-1360 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
P020BBA10 | P020BUA10 110VDC DISTRIBUTION A | P020BBA10 SGW 11kV SWITCHBOARD BUS A - 110V SUPPLY A | 6mm2 | 2C+E |  | ELE-SLD-1330 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
P020BBA10 | P020BUA10 110VDC DISTRIBUTION A | P020BBA10 SGW 11kV SWITCHBOARD BUS B - 110V SUPPLY A | 6mm2 | 2C+E |  | ELE-SLD-1330 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
P020BBA10 | P020BUB10 110VDC DISTRIBUTION B | P020BBA10 SGW 11kV SWITCHBOARD BUS A - 110V SUPPLY B | 6mm2 | 2C+E |  | ELE-SLD-1330 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
P020BBA10 | P020BUB10 110VDC DISTRIBUTION B | P020BBA10 SGW 11kV SWITCHBOARD BUS B - 110V SUPPLY B | 6mm2 | 2C+E |  | ELE-SLD-1330 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA10 | P020BBA10 11kV SWITCHGEAR BUS A | P020BFA10 SGW 400V SWITCHBOARD | 1.5mm2 | 12C+E |  | ELE-SDG-1160 | 25 | Power SGW | Cu PVC/PVC 0.6/1kV
P020BFA10 | P020BBA10 11kV SWITCHGEAR BUS B | P020BFA10 SGW 400V SWITCHBOARD | 1.5mm2 | 12C+E |  | ELE-SDG-1160 | 25 | Power SGW | Cu PVC/PVC 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A | 4mm2 | 2C+E |  | ELE-SLD-1300 | 50 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B | 4mm2 | 2C+E |  | ELE-SLD-1300 | 60 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A N | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A N | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A N | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A N | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B N | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B N | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B N | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B N | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L3 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L1 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L2 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L3 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L1 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L2 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L3 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L1 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L2 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L3 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L1 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT010 SGW Local Services Transformer 1 | P020BFA10 SGW AUXILIARY INCOMER A L2 | 630mm2 | 1C |  | ELE-SLD-1300 | 35 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L3 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L1 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L2 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L3 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L1 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L2 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L3 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L1 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L2 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L3 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L1 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFT10GT020 SGW Local Services Transformer 2 | P020BFA10 SGW AUXILIARY INCOMER B L2 | 630mm2 | 1C |  | ELE-SLD-1300 | 51 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFV10 Emergency Diesel Generator A Temporary JB | P020BFA10 SGW EDG INCOMER A | 70mm2 | 4C+E |  | ELE-SLD-1300 | 32 | Power SGW | ex Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BFV20 Emergency Diesel Generator B Temporary JB | P020BFA10 SGW EDG INCOMER B | 70mm2 | 4C+E |  | ELE-SLD-1300 | 32 | Power SGW | ex Cu XLPE/Rubber 0.6/1kV
P020BFA10 | P020BUA10 110VDC DISTRIBUTION A | P020BFA10 SGW 400V SWITCHBOARD BUS A - 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020BFA10 | P020BUA10 110VDC DISTRIBUTION A | P020BFA10 SGW 400V SWITCHBOARD BUS B - 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020BFA10 | P020BUB10 110VDC DISTRIBUTION B | P020BFA10 SGW 400V SWITCHBOARD BUS A - 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020BFA10 | P020BUB10 110VDC DISTRIBUTION B | P020BFA10 SGW 400V SWITCHBOARD BUS B - 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020BFA20_-F01 | P020BFA20 General Lighting and Power Panel A | P020BFA20_-F01 Outdoor Plant Lighting Circuit SGW Pump Station | 4mm2 | 2C+E |  | ELE-SLD-1400 | 200 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA20_-F03 | P020BFA20 General Lighting and Power Panel A | P020BFA20_-F03 Outdoor Plant Lighting Circuit SGW Building - Emerg | 4mm2 | 2C+E |  | ELE-SLD-1400 | 120 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA20_-F04 | P020BFA20 General Lighting and Power Panel A | P020BFA20_-F04 Outdoor Plant Lighting Circuit Vent Station | 10mm2 | 2C+E |  | ELE-SLD-1400 | 350 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA20_-F05 | P020BFA20 General Lighting and Power Panel A | P020BFA20_-F05 Outdoor Plant Lighting Circuit SGW Building - Transformer | 4mm2 | 2C+E |  | ELE-SLD-1400 | 150 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA20_-F11 | P020BFA20 General Lighting and Power Panel A | P020BFA20_-F11 Outdoor General Socket (1Ph) SGW Building | 4mm2 | 2C+E |  | ELE-SLD-1400 | 100 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA20_-F13 | P020BFA20 General Lighting and Power Panel A | P020BFA20_-F13 Outdoor General Socket (63A) Vent Station | 25mm2 | 4C+E |  | ELE-SLD-1400 | 75 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA20 | P020BFA10 SGW 400V SWITCHBOARD | P020BFA20 General Lighting and Power Panel A | 70mm2 | 4C+E |  | ELE-SLD-1303, ELE-SLD-1400 | 20 | Power SGW | ex Cu XLPE/Rubber 0.6/1kV
P020BFA30_-F01 | P020BFA30 General Lighting and Power Panel B | P020BFA30_-F01 Outdoor Plant Lighting Circuit SGW Pump Station | 4mm2 | 2C+E |  | ELE-SLD-1410 | 120 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA30_-F02 | P020BFA30 General Lighting and Power Panel B | P020BFA30_-F02 Outdoor Plant Lighting Circuit SGW Building / Transformer | 4mm2 | 2C+E |  | ELE-SLD-1410 | 150 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA30_-F03 | P020BFA30 General Lighting and Power Panel B | P020BFA30_-F03 Outdoor Plant Lighting Circuit GFHP Pump Station | 4mm2 | 2C+E |  | ELE-SLD-1410 | 200 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA30_-F04 | P020BFA30 General Lighting and Power Panel B | P020BFA30_-F04 Outdoor Plant Lighting Circuit Vent Station - 1st JB | 10mm2 | 2C+E |  | ELE-SLD-1410 | 150 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA30_-F04 | P020BFA30_-F04 Outdoor Plant Lighting Circuit Vent Station - 1st JB | P020BFA30_-F04 Outdoor Plant Lighting Circuit Vent Station - Last JB | 6mm2 | 2C+E |  | ELE-SLD-1410 | 200 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA30_-F05 | P020BFA30 General Lighting and Power Panel B | P020BFA30_-F05 Outdoor Plant Lighting Circuit Seal Water Tank Area | 4mm2 | 2C+E |  | ELE-SLD-1410 | 120 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA30_-F11 | P020BFA30 General Lighting and Power Panel B | P020BFA30_-F11 Outdoor General Socket (16A) Vent Station | 25mm2 | 2C+E |  | ELE-SLD-1410 | 220 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA30_-F13 | P020BFA30 General Lighting and Power Panel B | P020BFA30_-F13 Outdoor General Socket (63A) SGW Pump Station | 25mm2 | 4C+E |  | ELE-SLD-1410 | 70 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFA30 | P020BFA10 SGW 400V SWITCHBOARD | P020BFA30 General Lighting and Power Panel B | 70mm2 | 4C+E |  | ELE-SLD-1312, ELE-SLD-1410 | 20 | Power SGW | ex Cu XLPE/Rubber 0.6/1kV
P020BFA40 | P020BFA10 SGW 400V SWITCHBOARD | P020BFA40 Process DB A | 70mm2 | 4C+E |  | ELE-SLD-1303, ELE-SLD-1350 | 20 | Power SGW | ex Cu XLPE/Rubber 0.6/1kV
P020BFE10GT010 | P020BBA10 11kV SWITCHGEAR BUS A | P020BFE10GT010 SGW Pump A VSD Transformer | 1.5mm2 | 12C+E |  | ELE-SDG-1161 | 78 | Power SGW | Cu PVC/PVC 0.6/1kV
P020BFE10GT010 | P020BBA10 11kV SWITCHGEAR BUS A | P020BFE10GT010 SGW Pump A VSD Transformer | 120mm2 | 3C |  | ELE-RTD-1700 to 1723 | 60 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BFE10GT020 | P020BBA10 11kV SWITCHGEAR BUS B | P020BFE10GT020 SGW Pump B VSD Transformer | 1.5mm2 | 12C+E |  | ELE-SDG-1161 | 78 | Power SGW | Cu PVC/PVC 0.6/1kV
P020BFE10GT020 | P020BBA10 11kV SWITCHGEAR BUS B | P020BFE10GT020 SGW Pump B VSD Transformer | 120mm2 | 3C |  | BBA-ELE-SLD-1003 | 60 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BFE10GT030 | P020BBA10 11kV SWITCHGEAR BUS B | P020BFE10GT030 SGW Pump C VSD Transformer | 1.5mm2 | 12C+E |  | ELE-SDG-1161 | 78 | Power SGW | Cu PVC/PVC 0.6/1kV
P020BFE10GT030 | P020BBA10 11kV SWITCHGEAR BUS B | P020BFE10GT030 SGW Pump C VSD Transformer | 120mm2 | 3C |  | BBA-ELE-SLD-1003 | 60 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BFE10GU010_-M01 | P020BFA10 SGW 400V SWITCHBOARD | P020BFE10GU010_-M01 SGW Pump A VSD Coolant Pump | 6mm2 | 3C+E |  | ELE-SLD-1302 | 40 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFE10GU010 | P020BFE10GT010 SGW Pump A VSD Transformer | P020BFE10G_-U010 VSD SGW PUMP A | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1002, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU010 | P020BFE10GT010 SGW Pump A VSD Transformer | P020BFE10G_-U010 VSD SGW PUMP A | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1002, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU010 | P020BFE10GT010 SGW Pump A VSD Transformer | P020BFE10G_-U010 VSD SGW PUMP A | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1002, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU010 | P020BFE10GT010 SGW Pump A VSD Transformer | P020BFE10G_-U010 VSD SGW PUMP A | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1002, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU010 | P02BFA40 Process DB A | P020BFE10G_-U010 VSD SGW PUMP A Heater | 4mm2 | 2C+E |  | ELE-SLD-1350 | 30 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFE10GU010 | P02BFA40 Process DB A | P020BFE10G_-U010 VSD SGW PUMP A Auxiliary | 4mm2 | 2C+E |  | ELE-SLD-1350 | 30 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFE10GU020_-M01 | P020BFA10 SGW 400V SWITCHBOARD | P020BFE10GU020_-M01 SGW Pump B VSD Coolant Pump | 6mm2 | 3C+E |  | ELE-SLD-1311 | 40 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFE10GU020 | P020BFE10GT020 SGW Pump B VSD Transformer | P020BFE10G_-U020 VSD SGW PUMP B | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU020 | P020BFE10GT020 SGW Pump B VSD Transformer | P020BFE10G_-U020 VSD SGW PUMP B | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU020 | P020BFE10GT020 SGW Pump B VSD Transformer | P020BFE10G_-U020 VSD SGW PUMP B | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU020 | P020BFE10GT020 SGW Pump B VSD Transformer | P020BFE10G_-U020 VSD SGW PUMP B | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU020 | P020BFA50 Process DB B | P020BFE10G_-U020 VSD SGW PUMP B Heater | 4mm2 | 2C+E |  | ELE-SLD-1360 | 30 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFE10GU020 | P020BFA50 Process DB B | P020BFE10G_-U020 VSD SGW PUMP B Auxiliary | 4mm2 | 2C+E |  | ELE-SLD-1360 | 30 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFE10GU030_-M01 | P020BFA10 SGW 400V SWITCHBOARD | P020BFE10GU030_-M01 SGW Pump C VSD Coolant Pump | 6mm2 | 3C+E |  | ELE-SLD-1311 | 40 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFE10GU030 | P020BFE10GT030 SGW Pump C VSD Transformer | P020BFE10G_-U030 VSD SGW PUMP C | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU030 | P020BFE10GT030 SGW Pump C VSD Transformer | P020BFE10G_-U030 VSD SGW PUMP C | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU030 | P020BFE10GT030 SGW Pump C VSD Transformer | P020BFE10G_-U030 VSD SGW PUMP C | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU030 | P020BFE10GT030 SGW Pump C VSD Transformer | P020BFE10G_-U030 VSD SGW PUMP C | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 40 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020BFE10GU030 | P02BFA50 Process DB B | P020BFE10G_-U030 VSD SGW PUMP C Heater | 4mm2 | 2C+E |  | ELE-SLD-1360 | 30 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFE10GU030 | P02BFA50 Process DB B | P020BFE10G_-U030 VSD SGW PUMP C Auxiliary | 4mm2 | 2C+E |  | ELE-SLD-1360 | 30 | Power SGW | XLPE/LSZH 0.6/1kV
P020BFT10GT010 | P020BBA10 11kV SWITCHGEAR BUS A | P020BFT10GT010 SGW Local Services Transformer 1 | 1.5mm2 | 12C+E |  | ELE-SDG-1160 | 78 | Power SGW | Cu PVC/PVC 0.6/1kV
P020BFT10GT010 | P020BBA10 11kV SWITCHGEAR BUS A | P020BFT10GT010 SGW Local Services Transformer 1 | 120mm2 | 3C |  | BBA-ELE-SLD-1002 | 60 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BFT10GT020 | P020BBA10 11kV SWITCHGEAR BUS B | P020BFT10GT020 SGW Local Services Transformer 2 | 1.5mm2 | 12C+E |  | ELE-SDG-1160 | 78 | Power SGW | Cu PVC/PVC 0.6/1kV
P020BFT10GT020 | P020BBA10 11kV SWITCHGEAR BUS B | P020BFT10GT020 SGW Local Services Transformer 2 | 120mm2 | 3C |  | BBA-ELE-SLD-1003 | 60 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
P020BRA10 | P020BUA10 110VDC DISTRIBUTION A | P020BRA10 SGW 230VAC UPS A | 25mm2 | 2C+E |  | ELE-SLD-1330 | 11 | Power SGW | XLPE/LSZH 0.6/1kV
P020BRA10 | P020BFA10 SGW 400V SWITCHBOARD | P020BRA10 UPS System A Bypass Supply | 6mm2 | 2C+E |  | ELE-SLD-1303 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
P020BRB10 | P020BUB10 110VDC DISTRIBUTION B | P020BRB10 SGW 230VAC UPS B | 25mm2 | 2C+E |  | ELE-SLD-1330 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
P020BRB10 | P020BFA10 SGW 400V SWITCHBOARD | P020BRB10 UPS System B Bypass Supply | 6mm2 | 2C+E |  | ELE-SLD-1312 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
P020BTA10GA001 | P020BTA10 110V DC BATTERY A | P020BTA10GA001 BATTERY A FUSE BOX | 240mm2 | 2C |  | ELE-SLD-1330 | 10 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BTB10GA001 | P020BTB10 110V DC BATTERY B | P020BTB10GA001 BATTERY B FUSE BOX | 240mm2 | 2C |  | ELE-SLD-1330 | 10 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BTL10 | P020BFA10 SGW 400V SWITCHBOARD | P020BTL10 110VDC Power Supply System A Battery Charger | 10mm2 | 4C+E |  | ELE-SLD-1303 | 32 | Power SGW | XLPE/LSZH 0.6/1kV
P020BTL10 | P020BTA10GA001 BATTERY A FUSE BOX | P020BTL10 110VDC Power Supply System A Battery Charger | 240mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BTM10 | P020BFA10 SGW 400V SWITCHBOARD | P020BTM10 110VDC Power Supply System B Battery Charger | 10mm2 | 4C+E |  | ELE-SLD-1312 | 40 | Power SGW | XLPE/LSZH 0.6/1kV
P020BTM10 | P020BTB10GA001 BATTERY B FUSE BOX | P020BTM10 110VDC Power Supply System B Battery Charger | 240mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020BTM10 | P020BTL10 110VDC Power Supply System A Battery Charger | P020BTM10 110VDC Power Supply System B Battery Charger | 240mm2 | 2C |  | ELE-SLD-1330 | 11 | Power SGW | x Cu XLPE/Rubber 0.6/1kV
P020CRA10 | P020BUA10 110VDC DISTRIBUTION A | P020CRA10 PLC CABINET - COMMS 110V A SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUA10 110VDC DISTRIBUTION A | P020CRA10 PLC CABINET - IO CLUSTER 1 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUA10 110VDC DISTRIBUTION A | P020CRA10 PLC CABINET - IO CLUSTER 2 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUA10 110VDC DISTRIBUTION A | P020CRA10 PLC CABINET - IO CLUSTER 3 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUA10 110VDC DISTRIBUTION A | P020CRA10 PLC CABINET - IO CLUSTER 4 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUA10 110VDC DISTRIBUTION A | P020CRA10 PLC CABINET - IO CLUSTER 5 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUA10 110VDC DISTRIBUTION A | P020CRA10 PLC CABINET - IO CLUSTER 6 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUA10 110VDC DISTRIBUTION A | P020CRA10 VIBRATION CONTROL RACK | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUB10 110VDC DISTRIBUTION B | P020CRA10 PLC CABINET - COMMS 110V B SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUB10 110VDC DISTRIBUTION B | P020CRA10 PLC CABINET - IO CLUSTER 1 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUB10 110VDC DISTRIBUTION B | P020CRA10 PLC CABINET - IO CLUSTER 2 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUB10 110VDC DISTRIBUTION B | P020CRA10 PLC CABINET - IO CLUSTER 3 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUB10 110VDC DISTRIBUTION B | P020CRA10 PLC CABINET - IO CLUSTER 14110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUB10 110VDC DISTRIBUTION B | P020CRA10 PLC CABINET - IO CLUSTER 5 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUB10 110VDC DISTRIBUTION B | P020CRA10 PLC CABINET - IO CLUSTER 6 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BUB10 110VDC DISTRIBUTION B | P020CRA10 VIBRATION CONTROL RACK 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRA10 | P020BRC10 SGW 230VAC UPS A DB | P020CRA10 CS SERVER SUPPLY A | 2.5mm2 | 2C+E |  | ELE-SLD-1340 | 25 | Power SGW | u XLPE/LSZH 0.6/1kV
P020CRA10 | P020BRC10 SGW 230VAC UPS A DB | P020CRA10 OWS WORKSTATION SUPPLY A | 2.5mm2 | 2C+E |  | ELE-SLD-1340 | 25 | Power SGW | u XLPE/LSZH 0.6/1kV
P020CRA10 | P020BRD10 SGW 230VAC UPS B DB | P020CRA10 CS SERVER SUPPLY B | 2.5mm2 | 2C+E |  | ELE-SLD-1340 | 25 | Power SGW | u XLPE/LSZH 0.6/1kV
P020CRA10 | P020BRC10 SGW 230VAC UPS A DB | P020CRA10 OWS WORKSTATION SUPPLY B | 2.5mm2 | 2C+E |  | ELE-SLD-1340 | 25 | Power SGW | u XLPE/LSZH 0.6/1kV
P020CRS10 | P020BUA10 110VDC DISTRIBUTION A | P020CRS10 NETWORK CABINET - COMMS 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRS10 | P020BUB10 110VDC DISTRIBUTION B | P020CRS10 NETWORK CABINET - COMMS 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRS30 | P020BUA10 110VDC DISTRIBUTION A | P020CRS30 NETWORK CABINET - SERVERS 110V SUPPLY A | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRS30 | P020BUB10 110VDC DISTRIBUTION B | P020CRS30 NETWORK CABINET - SERVERS 110V SUPPLY B | 4mm2 | 2C |  | ELE-SLD-1330 | 20 | Power SGW | PE/LSZH 0.6/1kV
P020CRS30 | P020BRC10 SGW 230VAC UPS A DB | P020CRS30 BUILDING SERVICES SUPPLY A | 2.5mm2 | 2C+E |  | ELE-SLD-1340 | 25 | Power SGW | u XLPE/LSZH 0.6/1kV
P020CRS30 | P020BRC10 SGW 230VAC UPS A DB | P020CRS30 BUILDING SERVICES SUPPLY B | 2.5mm2 | 2C+E |  | ELE-SLD-1340 | 25 | Power SGW | u XLPE/LSZH 0.6/1kV
P020CRU10 | P020BRC10 SGW 230VAC UPS A DB | P020CRU10 OWS KVM SUPPLY A | 2.5mm2 | 2C+E |  | ELE-SLD-1340 | 25 | Power SGW | u XLPE/LSZH 0.6/1kV
P020CRU10 | P020BRD10 SGW 230VAC UPS B DB | P020CRU10 OWS KVM SUPPLY B | 2.5mm2 | 2C+E |  | ELE-SLD-1340 | 25 | Power SGW | u XLPE/LSZH 0.6/1kV
P020GWA20AP020_M01 | P020BFA10 SGW 400V SWITCHBOARD | P020GWA20AP020_M01 Seal Water Bund Sump Pump Motor | 6mm2 | 3C+E |  | ELE-SLD-1310 | 48 | Power SGW | XLPE/LSZH 0.6/1kV
P020GWA22AP010_-E01 | P020GAC20AP010_-U01 Seal Water Supply Pump A VSD | P020GWA22AP010_-E01 Seal Water Supply Pump A Motor E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-1301 | 70 | Power SGW | u PVC/PVC 0.6/1kV
P020GWA22AP010_M01 | P020GAC20AP010_-U01 Seal Water Supply Pump A VSD | P020GWA22AP010_M01 Seal Water Supply Pump A Motor | 6mm2 | 3C+3E |  | ELE-SLD-1301 | 45 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020GWA22AP010_-U01 | P020BFA10 SGW 400V SWITCHBOARD | P020GWA22AP010_-U01 Seal Water Supply Pump A VSD | 6mm2 | 3C+3E |  | ELE-SLD-1301 | 25 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020GWA22AP020_-E01 | P020GAC20AP020_-U01 Seal Water Supply Pump B VSD | P020GWA22AP020_-E01 Seal Water Supply Pump B Motor E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-1310 | 70 | Power SGW | u PVC/PVC 0.6/1kV
P020GWA22AP020_M01 | P020GAC20AP020_-U01 Seal Water Supply Pump B VSD | P020GWA22AP020_M01 Seal Water Supply Pump B Motor | 6mm2 | 3C+3E |  | ELE-SLD-1310 | 45 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020GWA22AP020_-U01 | P020BFA10 SGW 400V SWITCHBOARD | P020GWA22AP020_-U01 Seal Water Supply Pump B VSD | 6mm2 | 3C+3E |  | ELE-SLD-1310 | 25 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020GWA22AP030_-E01 | P020GAC20AP020_-U01 Seal Water Supply Pump C VSD | P020GWA22AP030_-E01 Seal Water Supply Pump C Motor E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-1310 | 70 | Power SGW | u PVC/PVC 0.6/1kV
P020GWA22AP030_M01 | P020GAC20AP020_-U01 Seal Water Supply Pump C VSD | P020GWA22AP030_M01 Seal Water Supply Pump C Motor | 6mm2 | 3C+3E |  | ELE-SLD-1310 | 45 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020GWA22AP030_-U01 | P020BFA10 SGW 400V SWITCHBOARD | P020GWA22AP030_-U01 Seal Water Supply Pump C VSD | 6mm2 | 3C+3E |  | ELE-SLD-1310 | 25 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020GWA30AH010_M01 | P020BFA10 SGW 400V SWITCHBOARD | P020GWA30AH010_M01 Seal Water Fin Fan Motor | 6mm2 | 3C+E |  | ELE-SLD-1310 | 46 | Power SGW | XLPE/LSZH 0.6/1kV
P020LFC20AA010 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AA010 GFHP Pump A Discharge Valve | 6mm2 | 3C+E |  | ELE-SLD-1302 | 90 | Power SGW | XLPE/LSZH 0.6/1kV
P020LFC20AA020 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AA020 GFHP Pump B Discharge Valve | 6mm2 | 3C+E |  | ELE-SLD-1311 | 90 | Power SGW | XLPE/LSZH 0.6/1kV
P020LFC20AP010_-E01 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AP010_-E01 GFHP Pump A Motor E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-1301 | 160 | Power SGW | u PVC/PVC 0.6/1kV
P020LFC20AP010_-H01 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AP010_-H01 GFHP Pump A Motor Heater | 4mm2 | 2C+E |  | ELE-SLD-1301 | 160 | Power SGW | XLPE/LSZH 0.6/1kV
P020LFC20AP010_-M01 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AP010_-M01 GFHP Pump A Motor | 240mm2 | 3C+E |  | ELE-SLD-1301 | 160 | Power SGW | lex Cu XLPE/Rubber 0.6/1kV
P020LFC20AP010_-M01 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AP010_-M01 GFHP Pump A Motor | 240mm2 | 3C+E |  | ELE-SLD-1301 | 160 | Power SGW | lex Cu XLPE/Rubber 0.6/1kV
P020LFC20AP020_-E01 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AP020_-E01 GFHP Pump B Motor E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-1310 | 170 | Power SGW | u PVC/PVC 0.6/1kV
P020LFC20AP020_-H01 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AP010_-H01 GFHP Pump B Motor Heater | 4mm2 | 2C+E |  | ELE-SLD-1310 | 170 | Power SGW | XLPE/LSZH 0.6/1kV
P020LFC20AP020_-M01 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AP020_-M01 GFHP Pump B Motor | 240mm2 | 3C+E |  | ELE-SLD-1310 | 170 | Power SGW | lex Cu XLPE/Rubber 0.6/1kV
P020LFC20AP020_-M01 | P020BFA10 SGW 400V SWITCHBOARD | P020LFC20AP020_-M01 GFHP Pump B Motor | 240mm2 | 3C+E |  | ELE-SLD-1310 | 170 | Power SGW | lex Cu XLPE/Rubber 0.6/1kV
P020NAB10AA030 | P020BFA10 SGW 400V SWITCHBOARD | P020NAB10AA030 Condensate Pump A Discharge Valve 1 | 6mm2 | 3C+E |  | ELE-SLD-1302 | 70 | Power SGW | XLPE/LSZH 0.6/1kV
P020NAB10AA110 | P020BFA10 SGW 400V SWITCHBOARD | P020NAB10AA110 Condensate Bypass Valve | 6mm2 | 3C+E |  | ELE-SLD-1302 | 75 | Power SGW | XLPE/LSZH 0.6/1kV
P020NAB10AP010_-E01 | P020NAB10AP010_-U01 Condensate Pump A VSD | P020NAB10AP010_-E01 Condensate Pump A Motor Control E-Stop | 1.5mm2 | 7C+E |  | ELE-SLD-1310 | 80 | Power SGW | u PVC/PVC 0.6/1kV
P020NAB10AP010_-H01 | P020NAB10AP010_-U01 Condensate Pump A VSD | P020NAB10AP010_-H01 Condensate Pump A Motor Heater | 4mm2 | 2C+E |  | ELE-SLD-1310 | 70 | Power SGW | XLPE/LSZH 0.6/1kV
P020NAB10AP010_-U01 | P02BFA50 Process DB B | P020NAB10AP010_-U01 Condensate Pump A VSD (Heater Supply) | 4mm2 | 2C+E |  | ELE-SLD-1360 | 15 | Power SGW | XLPE/LSZH 0.6/1kV
P020NAB10AP010M01 | P020NAB10AP010_-U01 Condensate Pump A VSD | P020NAB10AP010_M01 Condensate Pump A Motor | 95mm2 | 3C+3E |  | ELE-SLD-1310 | 65 | Power SGW | lex Cu XLPE/EMC/Rubber 0.6/1kV
P020NAB10AP010U01 | P020BFA10 SGW 400V SWITCHBOARD | P020NAB10AP010_-U01 Condensate Pump A VSD | 95mm2 | 3C+3E |  | ELE-SLD-1310 | 28 | Power SGW | lex Cu XLPE/EMC/Rubber 0.6/1kV
P020NDB10AA110 | P020BFA10 SGW 400V SWITCHBOARD | P020NDB10AA110 SGW Pump A VSD Discharge Valve | 6mm2 | 3C+E |  | ELE-SLD-1302 | 85 | Power SGW | XLPE/LSZH 0.6/1kV
P020NDB10AA120 | P020BFA10 SGW 400V SWITCHBOARD | P020NDB10AA120 SGW Pump B VSD Discharge Valve | 6mm2 | 3C+E |  | ELE-SLD-1311 | 85 | Power SGW | XLPE/LSZH 0.6/1kV
P020NDB10AA130 | P020BFA10 SGW 400V SWITCHBOARD | P020NDB10AA130 SGW Pump C VSD Discharge Valve | 6mm2 | 3C+E |  | ELE-SLD-1311 | 85 | Power SGW | XLPE/LSZH 0.6/1kV
P020NDB10AA140 | P020BFA10 SGW 400V SWITCHBOARD | P020NDB10AA140 SGW Pump Recirculation Valve | 6mm2 | 3C+E |  | ELE-SLD-1302 | 95 | Power SGW | XLPE/LSZH 0.6/1kV
P020NDB10AP010_-E01 | P020CRA10 PLC CABINET | P020NDB10AP010_-E01 SGW Pump A Motor E-Stop Push Button | 1.5mm2 | 12C+E |  | ELE-SDG-1145 | 70 | Power SGW | Cu PVC/PVC 0.6/1kV
P020NDB10AP010_-E01 | P020CRA10 PLC CABINET | S020CRA40 PLC SIS CABINET | 2.5mm2 | 12C+E |  | ELE-SDG-1145 | 550 | Power SGW | Cu PVC/PVC 0.6/1kV
P020NDB10AP010_-E01 | P020CRA10 PLC CABINET | P020BFE10G_-U020 VSD SGW PUMP B | 1.5mm2 | 12C+E |  | ELE-SDG-1145 | 25 | Power SGW | Cu PVC/PVC 0.6/1kV
P020NDB10AP010_-H01 | P020BFE10G_-U010 VSD SGW PUMP A | P020NDB10AP010_-H01 SGW Pump A Motor Heater | 4mm2 | 2C+E |  | ELE-SDG-1143 | 70 | Power SGW | XLPE/LSZH 0.6/1kV
P020NDB10AP010M01 | P020BFE10G_-U010 VSD SGW PUMP A | P020NDB10AP010_-M01 SGW Pump A Motor | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1002, ELE-SDG-1143 | 70 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020NDB10AP010M01 | P020BFE10G_-U010 VSD SGW PUMP A | P020NDB10AP010_-M01 SGW Pump A Motor | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1002, ELE-SDG-1143 | 70 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020NDB10AP010M01 | P020BFE10G_-U010 VSD SGW PUMP A | P020NDB10AP010_-M01 SGW Pump A Motor | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1002, ELE-SDG-1143 | 70 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020NDB10AP020_-E01 | P020CRA10 PLC CABINET | P020NDB10AP020_-E01 SGW Pump B Motor E-Stop Push Button | 1.5mm2 | 12C+E |  | ELE-SDG-1145 | 70 | Power SGW | Cu PVC/PVC 0.6/1kV
P020NDB10AP020_-E01 | P020CRA10 PLC CABINET | S020CRA40 PLC SIS CABINET | 2.5mm2 | 12C+E |  | ELE-SDG-1145 | 550 | Power SGW | Cu PVC/PVC 0.6/1kV
P020NDB10AP020_-E01 | P020CRA10 PLC CABINET | P020BFE10G_-U020 SGW VSD PUMP B | 1.5mm2 | 12C+E |  | ELE-SDG-1145 | 25 | Power SGW | Cu PVC/PVC 0.6/1kV
P020NDB10AP020_-H01 | P020BFE10G_-U020 VSD SGW PUMP B | P020NDB10AP020_-H01 SGW Pump B Motor Heater | 4mm2 | 2C+E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 70 | Power SGW | XLPE/LSZH 0.6/1kV
P020NDB10AP020M01 | P020BFE10G_-U020 VSD SGW PUMP B | P020NDB10AP020_-M01 SGW Pump B Motor | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 70 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020NDB10AP020M01 | P020BFE10G_-U020 VSD SGW PUMP B | P020NDB10AP020_-M01 SGW Pump B Motor | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 70 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020NDB10AP020M01 | P020BFE10G_-U020 VSD SGW PUMP B | P020NDB10AP020_-M01 SGW Pump B Motor | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 70 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020NDB10AP030_-H01 | P020CRA10 PLC CABINET | P020NDB10AP030_-H01 SGW Pump A Motor E-Stop Push Button | 1.5mm2 | 12C+E |  | ELE-SDG-1145 | 70 | Power SGW | Cu PVC/PVC 0.6/1kV
P020NDB10AP030_-H01 | P020CRA10 PLC CABINET | S020CRA40 PLC SIS CABINET | 2.5mm2 | 12C+E |  | ELE-SDG-1145 | 550 | Power SGW | Cu PVC/PVC 0.6/1kV
P020NDB10AP030_-H01 | P020CRA10 PLC CABINET | P020BFE10G_-U030 VSD SGW PUMP C | 1.5mm2 | 12C+E |  | ELE-SDG-1145 | 25 | Power SGW | Cu PVC/PVC 0.6/1kV
P020NDB10AP030_-H01 | P020BFE10G_-U030 VSD SGW PUMP C | P020NDB10AP030_-H01 SGW Pump C Motor Heater | 4mm2 | 2C+E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 70 | Power SGW | XLPE/LSZH 0.6/1kV
P020NDB10AP030M01 | P020BFE10G_-U030 VSD SGW PUMP C | P020NDB10AP030_-M01 SGW Pump C Motor | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 70 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020NDB10AP030M01 | P020BFE10G_-U030 VSD SGW PUMP C | P020NDB10AP030_-M01 SGW Pump C Motor | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 70 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020NDB10AP030M01 | P020BFE10G_-U030 VSD SGW PUMP C | P020NDB10AP030_-M01 SGW Pump C Motor | 400mm2 | 3C+3E |  | BBA-ELE-SLD-1003, ELE-SDG-1143 | 70 | Power SGW | Flex Cu XLPE/EMC/Rubber 0.6/1kV
P020PCB20AP010_-E01 | P020PCB20AP010_-U01 SGW Pump VSD Cooling Circ Pump A VSD | P020PCB20AP010_-E01 SGW Pump VSD Cooling Circ Pump A E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-1301 | 45 | Power SGW | u PVC/PVC 0.6/1kV
P020PCB20AP010_-M01 | P020PCB20AP010_-U01 SGW Pump VSD Cooling Circ Pump A VSD | P020PCB20AP010_-M01 SGW Pump VSD Cooling Circ Pump A Motor | 6mm2 | 3C+3E |  | ELE-SLD-1301 | 45 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020PCB20AP010_-U01 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB20AP010_-U01 SGW Pump VSD Cooling Circ Pump A VSD | 6mm2 | 3C+3E |  | ELE-SLD-1301 | 25 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020PCB20AP020_-E01 | P020PCB20AP020_-U01 SGW Pump VSD Cooling Circ Pump B VSD | P020PCB20AP020_-E01 SGW Pump VSD Cooling Circ Pump B E-Stop Push Button | 1.5mm2 | 7C+E |  | ELE-SLD-1310 | 45 | Power SGW | u PVC/PVC 0.6/1kV
P020PCB20AP020_M01 | P020PCB20AP020_-U01 SGW Pump VSD Cooling Circ Pump B VSD | P020PCB20AP020_M01 SGW Pump VSD Cooling Circ Pump B Motor | 6mm2 | 3C+3E |  | ELE-SLD-1310 | 45 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020PCB20AP020_-U01 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB20AP020_-U01 SGW Pump VSD Cooling Circ Pump B | 6mm2 | 3C+3E |  | ELE-SLD-1310 | 25 | Power SGW | ex Cu XLPE/EMC/Rubber 0.6/1kV
P020PCB20AP030_M01 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB20AP030_M01 SGW Building Sump Pump Motor | 6mm2 | 3C+E |  | ELE-SLD-1302 | 25 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB31AH010_-M01 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB31AH010_-M01 VSD Cooler A Fan 1 Motor | 6mm2 | 3C+E |  | ELE-SLD-1301 | 45 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB31AH010_-M02 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB31AH010_-M02 VSD Cooler A Fan 2 Motor | 6mm2 | 3C+E |  | ELE-SLD-1301 | 45 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB31AH010_-M03 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB31AH010_-M03 VSD Cooler A Fan 3 Motor | 6mm2 | 3C+E |  | ELE-SLD-1310 | 45 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB31AH010_-M04 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB31AH010_-M04 VSD Cooler A Fan 4 Motor | 6mm2 | 3C+E |  | ELE-SLD-1310 | 45 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB32AH020_-M01 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB32AH020_-M01 VSD Cooler B Fan 1 Motor | 6mm2 | 3C+E |  | ELE-SLD-1301 | 43 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB32AH020_-M02 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB32AH020_-M02 VSD Cooler B Fan 2 Motor | 6mm2 | 3C+E |  | ELE-SLD-1301 | 43 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB32AH020_-M03 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB32AH020_-M03 VSD Cooler B Fan 3 Motor | 6mm2 | 3C+E |  | ELE-SLD-1310 | 43 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB32AH020_-M04 | P020BFA10 SGW 400V SWITCHBOARD | P020PCB32AH020_-M04 VSD Cooler B Fan 4 Motor | 6mm2 | 3C+E |  | ELE-SLD-1310 | 43 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB33AH030_-M01 | P030BFA10 SGW 400V SWITCHBOARD | P020PCB33AH030_-M01 VSD Cooler C Fan 1 Motor | 6mm2 | 3C+E |  | ELE-SLD-1301 | 40 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB33AH030_-M02 | P030BFA10 SGW 400V SWITCHBOARD | P020PCB33AH030_-M02 VSD Cooler C Fan 2 Motor | 6mm2 | 3C+E |  | ELE-SLD-1301 | 40 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB33AH030_-M03 | P030BFA10 SGW 400V SWITCHBOARD | P020PCB33AH030_-M03 VSD Cooler C Fan 3 Motor | 6mm2 | 3C+E |  | ELE-SLD-1310 | 40 | Power SGW | XLPE/LSZH 0.6/1kV
P020PCB33AH030_-M04 | P030BFA10 SGW 400V SWITCHBOARD | P020PCB33AH030_-M04 VSD Cooler C Fan 4 Motor | 6mm2 | 3C+E |  | ELE-SLD-1310 | 40 | Power SGW | XLPE/LSZH 0.6/1kV
P020QFA10AN001 | P020BFA10 SGW 400V SWITCHBOARD | P020QFA10AN001 Compressor A + Dryer | 6mm2 | 3C+E |  | ELE-SLD-1303 | 30 | Power SGW | XLPE/LSZH 0.6/1kV
P020QFA10AN002 | P020BFA10 SGW 400V SWITCHBOARD | P020QFA10AN002 Compressor B + Dryer | 6mm2 | 3C+E |  | ELE-SLD-1312 | 30 | Power SGW | XLPE/LSZH 0.6/1kV
P020SAA10 | P020BFA10 SGW 400V SWITCHBOARD | P020SAA10 Building HVAC | 120mm2 | 4C+E |  | ELE-SLD-1303 | 32 | Power SGW | lex Cu XLPE/Rubber 0.6/1kV
P020SAB10 | P020BFA10 SGW 400V SWITCHBOARD | P020SAB10 Building HVAC | 120mm2 | 4C+E |  | ELE-SLD-1312 | 32 | Power SGW | lex Cu XLPE/Rubber 0.6/1kV
P02BFA50 | P020BFA10 SGW 400V SWITCHBOARD | P02BFA50 Process DB B | 70mm2 | 4C+E |  | ELE-SLD-1312, ELE-SLD-1360 | 20 | Power SGW | ex Cu XLPE/Rubber 0.6/1kV
S020BFT10GT020 | P020BBA10 11kV SWITCHGEAR BUS B | S020BFT10GT020 SP Local Services Transformer 2 | 120mm2 | 3C |  | BBA-ELE-SLD-1001 | 500 | Power SGW | XLPE/10KA/LSZH 6.35/11kV
S020GKA21BB050_H01 | P020BFA40 Process DB B | S020GKA21BB050_H01 Hot Water Cylinder Heater C (SGW Pump Building Battery Room) | 10mm2 | 4C+E |  | ELE-SLD-1350 | 20 | Power SGW | XLPE/LSZH 0.6/1kV
SGWMEB | P020BFT10GT010 SGW Local Services Transformer 1 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT010 SGW Local Services Transformer 1 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT010 SGW Local Services Transformer 1 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT010 SGW Local Services Transformer 1 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT010 SGW Local Services Transformer 1 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT010 SGW Local Services Transformer 1 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT020 SGW Local Services Transformer 2 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT020 SGW Local Services Transformer 2 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT020 SGW Local Services Transformer 2 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT020 SGW Local Services Transformer 2 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT020 SGW Local Services Transformer 2 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFT10GT020 SGW Local Services Transformer 2 | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 35 | Power SGW | PVC EARTH
SGWMEB | P020BFA10 SGW 400V SWITCHBOARD EARTH BAR | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFA10 SGW 400V SWITCHBOARD EARTH BAR | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFA10 SGW 400V SWITCHBOARD EARTH BAR | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFA10 SGW 400V SWITCHBOARD EARTH BAR | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 25 | Power SGW | PVC EARTH
SGWMEB | Column A2 BUILDING STRUCTURAL COLUMN | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0312 | 60 | Power SGW | PVC EARTH
SGWMEB | Column D3 BUILDING STRUCTURAL COLUMN | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0312 | 20 | Power SGW | PVC EARTH
SGWMEB | Column D7 BUILDING STRUCTURAL COLUMN | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0312 | 20 | Power SGW | PVC EARTH
SGWMEB | Column D8 BUILDING STRUCTURAL COLUMN | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0312 | 30 | Power SGW | PVC EARTH
SGWMEB | Wricon Building Structure Wricon | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0312 | 60 | Power SGW | PVC EARTH
SGWMEB | Wricon Building Structure Wricon | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0312 | 20 | Power SGW | PVC EARTH
SGWMEB | Wricon Building Structure Wricon | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0312 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT010 SGW Pump A Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT010 SGW Pump A Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT010 SGW Pump A Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT010 SGW Pump A Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT010 SGW Pump A Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT020 SGW Pump B Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT020 SGW Pump B Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT020 SGW Pump B Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT020 SGW Pump B Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT020 SGW Pump B Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT030 SGW Pump C Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT030 SGW Pump C Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT030 SGW Pump C Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT030 SGW Pump C Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10GT030 SGW Pump C Transformer | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 25 | Power SGW | PVC EARTH
SGWMEB | P020BFE10G_-U010 VSD SGW PUMP A | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BFE10G_-U010 VSD SGW PUMP A | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BFE10G_-U010 VSD SGW PUMP A | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BFE10G_-U020 VSD SGW PUMP B | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BFE10G_-U020 VSD SGW PUMP B | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BFE10G_-U020 VSD SGW PUMP B | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BFE10G_-U030 VSD SGW PUMP C | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BFE10G_-U030 VSD SGW PUMP C | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BFE10G_-U030 VSD SGW PUMP C | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0311 | 20 | Power SGW | PVC EARTH
SGWMEB | P020BTL10 110DC Charger A | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 25 | Power SGW | VC EARTH
SGWMEB | P020BTL10 110DC Battery A | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 25 | Power SGW | VC EARTH
SGWMEB | P020BTL10 110DC Charger B | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 25 | Power SGW | VC EARTH
SGWMEB | P020BTL10 110DC Battery B | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 25 | Power SGW | VC EARTH
SGWMEB | P020BRA10 SGW 230VAC UPS A | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 25 | Power SGW | VC EARTH
SGWMEB | P020BRB10 SGW 230VAC UPS B | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 25 | Power SGW | VC EARTH
SGWMEB | P020CRS10 NETWORK RACK A | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 30 | Power SGW | VC EARTH
SGWMEB | P020CRA30 NETWORK RACK B | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 30 | Power SGW | VC EARTH
SGWMEB | P020CRA10 CONTROL SYSTEM | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 30 | Power SGW | VC EARTH
SGWMEB | P020CRA10 CONTROL SYSTEM | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 30 | Power SGW | VC EARTH
SGWMEB | - SGW Pump A Cable Ladder | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 75 | Power SGW | VC EARTH
SGWMEB | - SGW Pump B Cable Ladder | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 75 | Power SGW | VC EARTH
SGWMEB | - SGW Pump C Cable Ladder | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 75 | Power SGW | VC EARTH
SGWMEB | - 11kV Cable Ladder (EPC) Steam Interface | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 200 | Power SGW | VC EARTH
SGWMEB | - 11kV Cable Ladder (EPC) Power Station Interface | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 200 | Power SGW | VC EARTH
SGWMEB | - 11kV Cable Ladder (Building) | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 100 | Power SGW | VC EARTH
SGWMEB | - 400V Cable Ladder (Building) | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 100 | Power SGW | VC EARTH
SGWMEB | - 400V Cable Ladder (EPC) | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 200 | Power SGW | VC EARTH
SGWMEB | - GFHP/Condensate Ladder | SGWMEB SGW BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | ELE-GND-0312 | 75 | Power SGW | VC EARTH
SGWMEB | SGW EARTH GRADIENT | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0312 | 60 | Power SGW | PVC EARTH
SGWMEB | SGW EARTH GRADIENT | SGWMEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0312 | 60 | Power SGW | PVC EARTH
SGWNEB | P020BBA10 11kV SWITCHGEAR EARTH BAR | SGWNEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 30 | Power SGW | PVC EARTH
SGWNEB | P020BBA10 11kV SWITCHGEAR EARTH BAR | SGWNEB SGW BUILDING MAIN EARTH BAR | 120mm2 | 1C |  | ELE-GND-0310 | 30 | Power SGW | PVC EARTH
0110BFA10_-C01 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110BFA10_-C01 3PH POWER SOCKET | 25mm2 | 4C+E |  | TH11-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0110BFA10_F112 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110BFA10_F112 H2S SCRUBBER | 4mm2 | 4C+E |  | TH11-1500-01 | 8 | Power Wellpads | XLPE/LSZH 0.6/1kV
0110BFA10_F113 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110BFA10_F113 INTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH11-1500-01 | 20 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0110BFA10_F114 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110BFA10_F114 EXTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH11-1500-01 | 40 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0110BFA10_F115 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110BFA10_F115 WELLPAD PLATFORM LIGHTING | 4mm2 | 2C+E |  | TH11-1500-01 | 50 | Power Wellpads | XLPE/LSZH 0.6/1kV
0110BFA10_F116 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110BFA10_F116 INTERNAL BUILDING SOCKET | 4mm2 | 2C+E |  | TH11-1500-01 | 60 | Power Wellpads | XLPE/LSZH 0.6/1kV
0110BFA10 | UNISON (TH11) WELLPAD POLE MOUNTED TRANSFORMER (UNISON) | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 95mm2 | 4C |  | TH11-1500-01, TH11-1000-01 | 150 | Power Wellpads | LPE/LSZH 0.6/1kV
0110BFA10 | 011BRV10 WELLPAD EDG CONNECTION | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 25mm2 | 4C+E |  | TH11-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0110BUA10 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110BUA10 110VDC SYSTEM | 4mm2 | 4C+E |  | TH11-1500-01 | 8 | Power Wellpads | XLPE/LSZH 0.6/1kV
0110CRA10 | 0110BUA10 110VDC SYSTEM | 0110CRA10 CONTROL SYSTEM POWER SUPPLY 1A | 4mm2 | 2C |  | TH11-1500-01 | 10 | Power Wellpads | PE/LSZH 0.6/1kV
0110CRA10 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110CRA10 CONTROL SYSTEM POWER SUPPLY 1B | 4mm2 | 2C+E |  | TH11-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0110CRA10 | 0110BUA10 110VDC SYSTEM | 0110CRA10 CONTROL SYSTEM POWER SUPPLY 2A | 4mm2 | 2C |  | TH11-1500-01 | 10 | Power Wellpads | PE/LSZH 0.6/1kV
0110CRA10 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110CRA10 CONTROL SYSTEM POWER SUPPLY 2B | 4mm2 | 2C+E |  | TH11-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0110CRA10 | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0110CRA10 CONTROL SYSTEM AUXILIARY SUPPLY | 4mm2 | 2C+E |  | TH11-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0110NAB10AA110 | 0110BUA10 110VDC SYSTEM | 0110NAB10AA110 TH11 FLOW CONTROL VALVE | 6mm2 | 2C |  | TH11-1500-01 | 50 | Power Wellpads | PE/LSZH 0.6/1kV
0120BFA10_-C01 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120BFA10_-C01 3PH POWER SOCKET | 25mm2 | 4C+E |  | TH12-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0120BFA10_F112 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120BFA10_F112 H2S SCRUBBER | 4mm2 | 4C+E |  | TH12-1500-01 | 8 | Power Wellpads | XLPE/LSZH 0.6/1kV
0120BFA10_F113 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120BFA10_F113 INTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH12-1500-01 | 20 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0120BFA10_F114 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120BFA10_F114 EXTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH12-1500-01 | 40 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0120BFA10_F115 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120BFA10_F115 WELLPAD PLATFORM LIGHTING | 4mm2 | 2C+E |  | TH12-1500-01 | 90 | Power Wellpads | XLPE/LSZH 0.6/1kV
0120BFA10_F116 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120BFA10_F116 INTERNAL BUILDING SOCKET | 4mm2 | 2C+E |  | TH12-1500-01 | 60 | Power Wellpads | XLPE/LSZH 0.6/1kV
0120BFA10 | TH000000AKA20GT010 WELLPAD POLE 25/1/1 POLE MOUNTED TRANSFORMER | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 95mm2 | 4C |  | TH12-1500-01, TH12-1000-01 | 160 | Power Wellpads | LPE/LSZH 0.6/1kV
0120BFA10 | 012BRV10 WELLPAD EDG CONNECTION | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 25mm2 | 4C+E |  | TH12-1500-01 | 20 | Power Wellpads | XLPE/LSZH 0.6/1kV
0120BUA10 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120BUA10 110VDC SYSTEM | 4mm2 | 3C+E |  | TH12-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0120CRA10 | 0120BUA10 110VDC SYSTEM | 0120CRA10 CONTROL SYSTEM POWER SUPPLY 1A | 4mm2 | 2C |  | TH12-1500-01 | 10 | Power Wellpads | PE/LSZH 0.6/1kV
0120CRA10 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120CRA10 CONTROL SYSTEM POWER SUPPLY 1B | 4mm2 | 2C+E |  | TH12-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0120CRA10 | 0120BUA10 110VDC SYSTEM | 0120CRA10 CONTROL SYSTEM POWER SUPPLY 2A | 4mm2 | 2C |  | TH12-1500-01 | 10 | Power Wellpads | PE/LSZH 0.6/1kV
0120CRA10 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120CRA10 CONTROL SYSTEM POWER SUPPLY 2B | 4mm2 | 2C+E |  | TH12-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0120CRA10 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120CRA10 CONTROL SYSTEM AUXILIARY SUPPLY | 4mm2 | 2C+E |  | TH12-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0120NDA10AA011 | 0120BUA10 110VDC SYSTEM | 0120NDA10AA011 TH12 ISOLATION VALVE | 10mm2 | 2C |  | TH12-1500-01 | 65 | Power Wellpads | LPE/LSZH 0.6/1kV
0120NDA10AA110 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0120NDA10AA110 TH12 ISOLATION VALVE | 6mm2 | 3C+E |  | TH12-1500-01 | 65 | Power Wellpads | XLPE/LSZH 0.6/1kV
0210NDA10AA011 | 0120BUA10 110VDC SYSTEM | 0210NDA10AA011 TH21 ISOLATION VALVE | 10mm2 | 2C |  | TH12-1500-01 | 90 | Power Wellpads | LPE/LSZH 0.6/1kV
0210NDA10AA110 | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0210NDA10AA110 TH21 ISOLATION VALVE | 6mm2 | 3C+E |  | TH12-1500-01 | 90 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260BFA10_-C01 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260BFA10_-C01 3PH POWER SOCKET | 25mm2 | 4C+E |  | TH26-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260BFA10_F112 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260BFA10_F112 H2S SCRUBBER | 4mm2 | 4C+E |  | TH26-1500-01 | 8 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260BFA10_F113 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260BFA10_F113 INTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH26-1500-01 | 20 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0260BFA10_F114 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260BFA10_F114 EXTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH26-1500-01 | 40 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0260BFA10_F115 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260BFA10_F115 WELLPAD PLATFORM LIGHTING | 4mm2 | 2C+E |  | TH26-1500-01 | 70 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260BFA10_F116 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260BFA10_F116 INTERNAL BUILDING SOCKET | 4mm2 | 2C+E |  | TH26-1500-01 | 60 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260BFA10 | TH000000AKA45GT010 WELLPAD POLE 42/18 POLE MOUNTED TRANSFORMER | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 95mm2 | 4C |  | TH26-1500-01, TH26-1000-01 | 60 | Power Wellpads | LPE/LSZH 0.6/1kV
0260BFA10 | 026BRV10 WELLPAD EDG CONNECTION | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 25mm2 | 4C+E |  | TH26-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260BUA10 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260BUA10 110VDC SYSTEM | 4mm2 | 4C+E |  | TH26-1500-01 | 8 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260CRA10 | 0260BUA10 110VDC SYSTEM | 0260CRA10 CONTROL SYSTEM POWER SUPPLY 1A | 4mm2 | 2C |  | TH26-1500-01 | 10 | Power Wellpads | PE/LSZH 0.6/1kV
0260CRA10 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260CRA10 CONTROL SYSTEM POWER SUPPLY 1B | 4mm2 | 2C+E |  | TH26-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260CRA10 | 0260BUA10 110VDC SYSTEM | 0260CRA10 CONTROL SYSTEM POWER SUPPLY 2A | 4mm2 | 2C |  | TH26-1500-01 | 10 | Power Wellpads | PE/LSZH 0.6/1kV
0260CRA10 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260CRA10 CONTROL SYSTEM POWER SUPPLY 2B | 4mm2 | 2C+E |  | TH26-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260CRA10 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260CRA10 CONTROL SYSTEM AUXILIARY SUPPLY | 4mm2 | 2C+E |  | TH26-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260NDA10AA011 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0260NDA10AA011 TH26 CONTROL VALVE | 6mm2 | 3C+E |  | TH26-1500-01 | 70 | Power Wellpads | XLPE/LSZH 0.6/1kV
0260NDA10AA110 | 0260BUA10 110VDC SYSTEM | 0260NDA10AA110 TH26 CONTROL VALVE | 10mm2 | 2C |  | TH26-1500-01 | 70 | Power Wellpads | LPE/LSZH 0.6/1kV
0280BFA10_-C01 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280BFA10_-C01 3PH POWER SOCKET | 25mm2 | 4C+E |  | TH28-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0280BFA10_F112 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280BFA10_F112 H2S SCRUBBER | 4mm2 | 4C+E |  | TH28-1500-01 | 8 | Power Wellpads | XLPE/LSZH 0.6/1kV
0280BFA10_F113 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280BFA10_F113 INTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH28-1500-01 | 20 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0280BFA10_F114 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280BFA10_F114 EXTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH28-1500-01 | 40 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0280BFA10_F115 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280BFA10_F115 WELLPAD PLATFORM LIGHTING | 4mm2 | 2C+E |  | TH28-1500-01 | 99 | Power Wellpads | XLPE/LSZH 0.6/1kV
0280BFA10_F116 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280BFA10_F116 INTERNAL BUILDING SOCKET | 4mm2 | 2C+E |  | TH28-1500-01 | 60 | Power Wellpads | XLPE/LSZH 0.6/1kV
0280BFA10 | TH000000AKA40GT010 WELLPAD POLE 41 POLE MOUNTED TRANSFORMER | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 95mm2 | 4C |  | TH28-1500-01, TH28-1000-01 | 120 | Power Wellpads | LPE/LSZH 0.6/1kV
0280BFA10 | 028BRV10 WELLPAD EDG CONNECTION | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 25mm2 | 4C+E |  | TH28-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0280BUA10 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280BUA10 110VDC SYSTEM | 4mm2 | 3C+E |  | TH28-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0280CRA10 | 0280BUA10 110VDC SYSTEM | 0280CRA10 CONTROL SYSTEM POWER SUPPLY 1A | 4mm2 | 2C |  | TH28-1500-01 | 20 | Power Wellpads | PE/LSZH 0.6/1kV
0280CRA10 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280CRA10 CONTROL SYSTEM POWER SUPPLY 1B | 4mm2 | 2C+E |  | TH28-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0280CRA10 | 0280BUA10 110VDC SYSTEM | 0280CRA10 CONTROL SYSTEM POWER SUPPLY 2A | 4mm2 | 2C |  | TH28-1500-01 | 10 | Power Wellpads | PE/LSZH 0.6/1kV
0280CRA10 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280CRA10 CONTROL SYSTEM POWER SUPPLY 2B | 4mm2 | 2C+E |  | TH28-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0280CRA10 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280CRA10 CONTROL SYSTEM AUXILIARY SUPPLY | 4mm2 | 2C+E |  | TH28-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0280NDA10AA011_-M01 | 0280BUA10 110VDC SYSTEM | 0280NDA10AA011_-M01 TH28 ISOLATION VALVE | 10mm2 | 2C |  | TH28-1500-01 | 99 | Power Wellpads | LPE/LSZH 0.6/1kV
0280NDA10AA110_-M01 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0280NDA10AA110_-M01 TH28 ISOLATION VALVE | 6mm2 | 3C+E |  | TH28-1500-01 | 99 | Power Wellpads | XLPE/LSZH 0.6/1kV
0290BFA10_-C01 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290BFA10_-C01 3PH POWER SOCKET | 25mm2 | 4C+E |  | TH29-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0290BFA10_F112 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290BFA10_F112 H2S SCRUBBER | 4mm2 | 4C+E |  | TH29-1500-01 | 8 | Power Wellpads | XLPE/LSZH 0.6/1kV
0290BFA10_F113 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290BFA10_F113 INTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH29-1500-01 | 20 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0290BFA10_F114 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290BFA10_F114 EXTERNAL BUILDING LIGHTING | 2.5mm2 | 2C+E |  | TH29-1500-01 | 40 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0290BFA10_F115 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290BFA10_F115 WELLPAD PLATFORM LIGHTING | 4mm2 | 2C+E |  | TH29-1500-01 | 95 | Power Wellpads | XLPE/LSZH 0.6/1kV
0290BFA10_F116 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290BFA10_F116 INTERNAL BUILDING SOCKET | 4mm2 | 2C+E |  | TH29-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0290BFA10 | UNISON (TH29) WELLPAD POLE42/18 POLE MOUNTED TRANSFORMER | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 95mm2 | 4C |  | TH29-1500-01, TH29-1000-01 | 100 | Power Wellpads | LPE/LSZH 0.6/1kV
0290BFA10 | 029BRV10 WELLPAD EDG CONNECTION | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 25mm2 | 4C+E |  | TH29-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0290BUA10 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290BUA10 110VDC SYSTEM | 4mm2 | 3C+E |  | TH29-1500-01 | 10 | Power Wellpads | XLPE/LSZH 0.6/1kV
0290CRA10 | 0290BUA10 110VDC SYSTEM | 0290CRA10 CONTROL SYSTEM POWER SUPPLY 1A | 4mm2 | 2C |  | TH29-1500-01 | 10 | Power Wellpads | PE/LSZH 0.6/1kV
0290CRA10 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290CRA10 CONTROL SYSTEM POWER SUPPLY 1B | 4mm2 | 2C+E |  | TH29-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0290CRA10 | 0290BUA10 110VDC SYSTEM | 0290CRA10 CONTROL SYSTEM POWER SUPPLY 2A | 4mm2 | 2C |  | TH29-1500-01 | 10 | Power Wellpads | PE/LSZH 0.6/1kV
0290CRA10 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290CRA10 CONTROL SYSTEM POWER SUPPLY 2B | 4mm2 | 2C+E |  | TH29-1500-01 | 15 | Power Wellpads | XLPE/LSZH 0.6/1kV
0290CRA10 | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0290CRA10 CONTROL SYSTEM AUXILIARY SUPPLY | 2.5mm2 | 2C+E |  | TH29-1500-01 | 20 | Power Wellpads | u XLPE/LSZH 0.6/1kV
0290NDB10AA110_-M01 | 0290BUA10 110VDC SYSTEM | 0290NDB10AA110_-M01 TH29 ISOLATION VALVE | 10mm2 | 2C |  | TH29-1500-01 | 83 | Power Wellpads | LPE/LSZH 0.6/1kV
0300NDA10AA011 | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0300NDA10AA011 TH30 CONTROL VALVE | 6mm2 | 3C+E |  | TH26-1500-01 | 84 | Power Wellpads | XLPE/LSZH 0.6/1kV
0300NDA10AA110 | 0260BUA10 110VDC SYSTEM | 0300NDA10AA110 TH30 CONTROL VALVE | 6mm2 | 2C |  | TH26-1500-01 | 45 | Power Wellpads | PE/LSZH 0.6/1kV
0310NDB10AA110_-M01 | 0290BUA10 110VDC SYSTEM | 0310NDB10AA110_-M01 TH31 ISOLATION VALVE | 10mm2 | 2C |  | TH29-1500-01 | 69 | Power Wellpads | LPE/LSZH 0.6/1kV
0340NDA10AA011_-M01 | 0280BUA10 110VDC SYSTEM | 0340NDA10AA011_-M01 TH34 ISOLATION VALVE | 10mm2 | 2C |  | TH28-1500-01 | 84 | Power Wellpads | LPE/LSZH 0.6/1kV
0340NDA10AA110_-M01 | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD | 0340NDA10AA110_-M01 TH34 ISOLATION VALVE | 6mm2 | 3C+E |  | TH28-1500-01 | 84 | Power Wellpads | XLPE/LSZH 0.6/1kV
0350NDB10AA110_-M01 | 0290BUA10 110VDC SYSTEM | 0350NDB10AA110_-M01 TH35 ISOLATION VALVE | 6mm2 | 2C |  | TH29-1500-01 | 49 | Power Wellpads | PE/LSZH 0.6/1kV
WPMEB | TH000000AKA45GT010 WELLPAD POLE 42/18 POLE MOUNTED TRANSFORMER EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TH26-1500-01, TH26-1000-01 | 60 | Power Wellpads | VC EARTH
WPMEB | UNISON (TH11) WELLPAD POLE MOUNTED TRANSFORMER FRAME EARTH (UNISON) | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TH11-1500-01, TH11-1000-01 | 150 | Power Wellpads | VC EARTH
WPMEB | TH000000AKA20GT010 WELLPAD POLE 25/1/1 POLE MOUNTED TRANSFORMER EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TH12-1500-01, TH12-1000-01 | 160 | Power Wellpads | VC EARTH
WPMEB | TH000000AKA40GT010 WELLPAD POLE 41 POLE MOUNTED TRANSFORMER FRAME EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TH28-1500-01, TH28-1000-01 | 120 | Power Wellpads | VC EARTH
WPMEB | UNISON (TH29) WELLPAD POLE42/18 POLE MOUNTED TRANSFORMER EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TH29-1500-01, TH29-1000-01 | 100 | Power Wellpads | VC EARTH
WPMEB | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TH26-1000-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TH11-1000-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TH12-1000-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0260BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0110BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0120BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0280BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0290BFA10 WELLPAD 400V/230V DISTRIBUTION BOARD FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0260BUA10 110VDC SYSTEM | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0110BUA10 110VDC SYSTEM | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0120BUA10 110VDC SYSTEM | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0280BUA10 110VDC SYSTEM | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0290BUA10 110VDC SYSTEM | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0260CRA10 CONTROL SYSTEM PANEL EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0110CRA10 CONTROL SYSTEM PANEL EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0120CRA10 CONTROL SYSTEM PANEL EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0280CRA10 CONTROL SYSTEM PANEL EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0290CRA10 CONTROL SYSTEM PANEL EARTH BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0260CRA10 CONTROL SYSTEM PANEL INSTRUMENT BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0110CRA10 CONTROL SYSTEM PANEL INSTRUMENT BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0120CRA10 CONTROL SYSTEM PANEL INSTRUMENT BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0280CRA10 CONTROL SYSTEM PANEL INSTRUMENT BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0290CRA10 CONTROL SYSTEM PANEL INSTRUMENT BAR | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0260CRA10 CONTROL SYSTEM PANEL FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0110CRA10 CONTROL SYSTEM PANEL FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0120CRA10 CONTROL SYSTEM PANEL FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0280CRA10 CONTROL SYSTEM PANEL FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | 0290CRA10 CONTROL SYSTEM PANEL FRAME | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING CABLE LADDER | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING CABLE LADDER | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING CABLE LADDER | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING CABLE LADDER | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING REINFORCEMENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING CABLE LADDER | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING REINFORCEMENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING REINFORCEMENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING REINFORCEMENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING FLOOR GRATING | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING REINFORCEMENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING REINFORCEMENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING FLOOR GRATING | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | - BUILDING FLOOR GRATING | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 5 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH26-1506-01 | 10 | Power Wellpads | VC EARTH
WPMEB | - BUILDING FLOOR GRATING | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01 | 5 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH12-1506-01 | 10 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 10 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 10 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH26-1506-01 | 10 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH11-1506-01 | 10 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH12-1506-01 | 10 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH28-1506-01 | 10 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH29-1506-01 | 10 | Power Wellpads | VC EARTH
WPMEB | WPEG EARTH GRADIENT | WPMEB WELLPAD BUILDING MAIN EARTH BAR | 70mm2 | 1C |  | TAS1-1505-01, TH11-1506-01 | 10 | Power Wellpads | VC EARTH

## Sheet1
Station | System | Tag | Point | Funct | Type | S/No | Criticality | ResCon | PECPR | KPI | NominalValue | Setting | Range | DeviceType | Proof | Loop | PlantCode | Data | StoresNo | DrawingNo | Procs | MVUnit | IdealUnit |  | MVar1 | MVar2 | MVar3 | MVar4 | MVar5 | MVar6 | MVar7 | IdO1 | IdO2 | IdO3 | IdO4 | IdO5 | IdO6 | IdO7 | Digi1 | Digi2 | Digi3 | Digi4 | Digi5 | Digi6 | DigiAliase1 | DigiAliase2 | DigiAliase3 | DigiAliase4 | DigiAliase5 | DigiAliase6 | DateChecked | CheckedBy
0110LFC10CL010 | Common Steam/Water Dump System | 10CL010 | Wellpad TH11 |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 6000 | - | 6000 | 6000 |  |  | TH11-7.5.001-01 | 0110LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-0033 |  | mm | mm | 6000 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
0110NAB10CF010 | Condensate System | 10CF010 | Wellpad TH11 |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ |  |  |  |  | 25 | 1000 | -1 1500 | -1 1500 |  |  | TH11-7.5.001-01 | 0110NAB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0033 |  | bar(g) |  | 1300
0110NAB10CP010 | Condensate System | 10CP010 | Wellpad TH11 |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 25 | 5.1 | -1 to 55 | 25 |  |  | TH11-7.5.001-01 | 0110NAB10CP010 | CCI-DAT-1461 |  | PRO-PID-0033 |  | bar(g) |  | 6000
0110NAB10CP510 | Condensate System | 10CP510 | Wellpad TH11 |  | Wika 72039878+14503369+0731277 |  |  |  |  | 1300 | 5.1 | 25 | - |  |  | 0 | 0110NAB10CP510 | CCI-DAT-1460 |  | PRO-PID-0033 |  | mm |  | 100 | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25
0110NAB10CP520 | Condensate System | 10CP520 | Wellpad TH11 |  | Wika 72039878+14503369+0731277 |  |  |  |  | 6000 | 5.1 | 25 | - |  |  | 0 | 0110NAB10CP520 | CCI-DAT-1460 |  | PRO-PID-0033 |  | mm |  | 770 | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25
0120LFC10CL010 | Common Steam/Water Dump System | 10CL010 | Wellpad TH12 |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 100 | 950 | 1300 | 1300 |  |  | TH12-8.5.002-01 | 0120LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-0037 |  | bar(g) |  | 100 | MVar1: 0; MVar2: 325; MVar3: 650; MVar4: 975; MVar5: 1300
0120LFC10CL020 | Common Steam/Water Dump System | 10CL020 | Wellpad TH12 |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 770 | 2350 | 6000 | 6000 |  |  | TH12-8.5.001-01 | 0120LFC10CL020 | CCI-DAT-1468 |  | PRO-PID-0037 |  | bar(g) |  | 100 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
0120LFC10CP010 | Common Steam/Water Dump System | 10CP010 | Wellpad TH12 |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 770 | 0 | -1 to 10.3 | 10 |  |  | TH12-8.5.002-01 | 0120LFC10CP010 | CCI-DAT-1461 |  | PRO-PID-0037 |  | bar(g) |  | 300
0120LFC10CP510 | Common Steam/Water Dump System | 10CP510 | Wellpad TH12 |  | Wika 72039884+14503369+0763349 |  |  |  |  | 100 | 30 | 100 | - |  |  | 0 | 0120LFC10CP510 | CCI-DAT-1460 |  | PRO-PID-0037 |  | mm |  | 770 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0120NDA10CF010 | Production Piping System | 10CF010 | Wellpad TH12 |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ |  |  |  |  | 100 | 699 | 770 | 770 |  |  | TH12-8.5.001-01 | 0120NDA10CF010 | CCI-DAT-1472 Note 2 |  | PRO-PID-0037 |  | bar(g) |  | 770 | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770
0120NDA10CF020 | Production Piping System | 10CF020 | Wellpad TH12 |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 |  |  |  |  | 300 | 699 | 770 | 770 |  |  | 0 | 0120NDA10CF020 | CCI-DAT-1472 Note 2 |  | PRO-PID-0037 |  | bar(g) |  | 100 | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770
0120NDA10CP010 | Production Piping System | 10CP010 | Wellpad TH12 |  | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 6000 | 0 | -1 to 75 | 75 |  |  | TH12-8.5.001-01 | 0120NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0037 |  | mm |  | 100
0120NDA10CP510 | Production Piping System | 10CP510 | Wellpad TH12 |  | Wika 72039884+14503369+0763349 |  |  |  |  | 770 | 30 | 100 | - |  |  | 0 | 0120NDA10CP510 | CCI-DAT-1460 |  | PRO-PID-0037 |  | mm |  | 300 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0120NDA10CP520 | Production Piping System | 10CP520 | Wellpad TH12 |  | Wika 72039884+14503369+0763349 |  |  |  |  | 770 | 30 | 100 | - |  |  | 0 | 0120NDA10CP520 | CCI-DAT-1460 |  | PRO-PID-0037 |  | bar(g) |  | 1300 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0120NDA10CT010 | Production Piping System | 10CT010 | Wellpad TH12 |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW |  |  |  |  | 100 | 235 | 300 | 300 |  |  | TH12-8.5.001-01 | 0120NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0037 |  | bar(g) |  | 100 | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300
0190LFC10CL010 | Common Steam/Water Dump System | 10CL010 | Wellpad TH19N |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 100 | - | 6000 | 6000 |  |  | 0 | 0190LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-0039 |  | bar(g) |  | 770 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
0210NDA10CF010 | Production Piping System | 10CF010 | Wellpad TH12 (TH21) |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ |  |  |  |  | 300 | 699 | 770 | 770 |  |  | TH12-8.5.002-01 | 0210NDA10CF010 | CCI-DAT-1472 Note 2 |  | PRO-PID-0037 |  | mm |  | 770 | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770
0210NDA10CF020 | Production Piping System | 10CF020 | Wellpad TH12 (TH21) |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 |  |  |  |  | 1300 | 699 | 770 | 770 |  |  | 0 | 0210NDA10CF020 | CCI-DAT-1472 Note 2 |  | PRO-PID-0037 |  | mm |  | 100 | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770
0210NDA10CP010 | Production Piping System | 10CP010 | Wellpad TH12 (TH21) |  | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 6000 | 30 | -1 to 75 | 75 |  |  | TH12-8.5.002-01 | 0210NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0037 |  | bar(g) |  | 100
0210NDA10CP510 | Production Piping System | 10CP510 | Wellpad TH12 (TH21) |  | Wika 72039884+14503369+0763349 |  |  |  |  | 100 | 30 | 100 | - |  |  | 0 | 0210NDA10CP510 | CCI-DAT-1460 |  | PRO-PID-0037 |  | bar(g) |  | 1300 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0210NDA10CP520 | Production Piping System | 10CP520 | Wellpad TH12 (TH21) |  | Wika 72039884+14503369+0763349 |  |  |  |  | 770 | 30 | 100 | - |  |  | 0 | 0210NDA10CP520 | CCI-DAT-1460 |  | PRO-PID-0037 |  | bar(g) |  | 6000 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0210NDA10CT010 | Production Piping System | 10CT010 | Wellpad TH12 (TH21) |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW |  |  |  |  | 770 | 235 | 300 | 300 |  |  | TH12-8.5.002-01 | 0210NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0037 |  | mm |  | 100 | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300
0260LFC10CL010 | Common Steam/Water Dump System | 10CL010 | Wellpad TH26 |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 100 | 950 | 1300 | 1300 |  |  | TH26-4.5.002-01 | 0260LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-0036 |  | bar(g) |  | 590 | MVar1: 0; MVar2: 325; MVar3: 650; MVar4: 975; MVar5: 1300
0260LFC10CL020 | Common Steam/Water Dump System | 10CL020 | Wellpad TH26 |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 100 | 2350 | 6000 | 6000 |  |  | TH26-4.5.001-01 | 0260LFC10CL020 | CCI-DAT-1468 |  | PRO-PID-0036 |  | bar(g) |  | 100 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
0260LFC10CP010 | Common Steam/Water Dump System | 10CP010 | Wellpad TH26 |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 300 | 0 | -1 to 10.3 | 10 |  |  | TH26-4.5.002-01 | 0260LFC10CP010 | CCI-DAT-1461 |  | PRO-PID-0036 |  | bar(g) |  | 100
0260LFC10CP510 | Common Steam/Water Dump System | 10CP510 | Wellpad TH26 |  | Wika 72039884+14503369+0763349 |  |  |  |  | 1300 | 30 | 100 | - |  |  | 0 | 0260LFC10CP510 | CCI-DAT-1460 |  | PRO-PID-0036 |  | bar(g) |  | 300 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0260NDA10CF010 | Production Piping System | 10CF010 | Wellpad TH26 |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ |  |  |  |  | 6000 | 699 | 770 | 770 |  |  | TH26-4.5.001-01 | 0260NDA10CF010 | CCI-DAT-1472 Note 2 |  | PRO-PID-0036 |  | bar(g) |  | 6000 | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770
0260NDA10CF020 | Production Piping System | 10CF020 | Wellpad TH26 |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 |  |  |  |  | 100 | 699 | 770 | 770 |  |  | 0 | 0260NDA10CF020 | CCI-DAT-1472 Note 2 |  | PRO-PID-0036 |  | bar(g) |  | 60 | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770
0260NDA10CP010 | Production Piping System | 10CP010 | Wellpad TH26 |  | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 590 | 0 | -1 to 75 | 75 |  |  | TH26-4.5.001-01 | 0260NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0036 |  | bar(g) |  | 770
0260NDA10CP510 | Production Piping System | 10CP510 | Wellpad TH26 |  | Wika 72039884+14503369+0763349 |  |  |  |  | 590 | 30 | 100 | - |  |  | 0 | 0260NDA10CP510 | CCI-DAT-1460 |  | PRO-PID-0036 |  | bar(g) |  | 770 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0260NDA10CP520 | Production Piping System | 10CP520 | Wellpad TH26 |  | Wika 72039884+14503369+0763349 |  |  |  |  | 100 | 30 | 100 | - |  |  | 0 | 0260NDA10CP520 | CCI-DAT-1460 |  | PRO-PID-0036 |  | bar(g) |  | 100 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0260NDA10CT010 | Production Piping System | 10CT010 | Wellpad TH26 |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW |  |  |  |  | 100 | 235 | 300 | 300 |  |  | TH26-4.5.001-01 | 0260NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0036 |  | bar(g) |  | 300 | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300
0280LFC10CL010 | Common Steam/Water Dump System | 10CL010 | Wellpad TH28 |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 300 | 950 | 1300 | 1300 |  |  | TH28-9.5.002-01 | 0280LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-0031 |  | bar(g) |  | 60 | MVar1: 0; MVar2: 325; MVar3: 650; MVar4: 975; MVar5: 1300
0280LFC10CL020 | Common Steam/Water Dump System | 10CL020 | Wellpad TH28 |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 6000 | 2350 | 6000 | 6000 |  |  | TH28-9.5.001-01 | 0280LFC10CL020 | CCI-DAT-1468 |  | PRO-PID-0031 |  | bar(g) |  | 60 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
0280LFC10CP010 | Common Steam/Water Dump System | 10CP010 | Wellpad TH28 |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 60 | 0 | -1 to 10.3 | 10 |  |  | TH28-9.5.002-01 | 0280LFC10CP010 | CCI-DAT-1461 |  | PRO-PID-0031 |  | bar(g) |  | 60
0280LFC10CP510 | Common Steam/Water Dump System | 10CP510 | Wellpad TH28 |  | Wika 72039884+14503369+0763349 |  |  |  |  | 60 | 30 | 100 | - |  |  | 0 | 0280LFC10CP510 | CCI-DAT-1460 |  | PRO-PID-0031 |  | bar(g) |  | 60 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0280NDA10CF010 | Production Piping System | 10CF010 | Wellpad TH28 |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ |  |  |  |  | 770 | 531 | 590 | 590 |  |  | TH28-9.5.001-01 | 0280NDA10CF010 | CCI-DAT-1472 Note 2 |  | PRO-PID-0031 |  | tph |  | 590 | MVar1: 0; MVar2: 147.5; MVar3: 295; MVar4: 442.5; MVar5: 590
0280NDA10CF020 | Production Piping System | 10CF020 | Wellpad TH28 |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 |  |  |  |  | 770 | 531 | 590 | 590 |  |  | 0 | 0280NDA10CF020 | CCI-DAT-1472 Note 2 |  | PRO-PID-0031 |  | bar(g) |  | 590 | MVar1: 0; MVar2: 147.5; MVar3: 295; MVar4: 442.5; MVar5: 590
0280NDA10CP010 | Production Piping System | 10CP010 | Wellpad TH28 |  | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 100 | 26.3 | -1 to 75 | 75 |  |  | TH28-9.5.001-01 | 0280NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0031 |  | bar(g) |  | 100
0280NDA10CP510 | Production Piping System | 10CP510 | Wellpad TH28 |  | Wika 72039884+14503369+0763349 |  |  |  |  | 100 | 26.3 | 100 | - |  |  | 0 | 0280NDA10CP510 | CCI-DAT-1460 |  | PRO-PID-0031 |  | bar(g) |  | 300 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0280NDA10CP520 | Production Piping System | 10CP520 | Wellpad TH28 |  | Wika 72039884+14503369+0763349 |  |  |  |  | 300 | 20.5 | 100 | - |  |  | 0 | 0280NDA10CP520 | CCI-DAT-1460 |  | PRO-PID-0031 |  | tph |  | 60 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0280NDA10CT010 | Production Piping System | 10CT010 | Wellpad TH28 |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW |  |  |  |  | 60 | 216 | 300 | 300 |  |  | TH28-9.5.001-01 | 0280NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0031 |  | bar(g) |  | 60 | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300
0290LFC10CL010 | Common Steam/Water Dump System | 10CL010 | Wellpad TH29 |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 60 | - | 6000 | 6000 |  |  | TH29-2.5.001-01 | 0290LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-0032 |  | bar(g) |  | 60 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
0290NDB10CF010 | Separated Water System | 10CF010 | Wellpad TH29 |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ |  |  |  |  | 60 | 370 | -5 to 410 | -5 to 410 |  |  | TH29-2.5.001-01 | 0290NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0032 |  | bar(g) |  | 60
0290NDB10CP010 | Separated Water System | 10CP010 | Wellpad TH29 |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 60 | 15 | -1 to 55 | 50 |  |  | TH29-2.5.001-01 | 0290NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0032 |  | tph |  | 60
0290NDB10CP510 | Separated Water System | 10CP510 | Wellpad TH29 |  | Wika 72039876+14503369+0731277 |  |  |  |  | 60 | 15 | 60 | - |  |  | 0 | 0290NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-0032 |  | bar(g) |  | 60 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0290NDB10CP520 | Separated Water System | 10CP520 | Wellpad TH29 |  | Wika 72039876+14503369+0731277 |  |  |  |  | 60 | 15 | 60 | - |  |  | 0 | 0290NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-0032 |  | bar(g) |  | 40 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0300NDA10CF010 | Production Piping System | 10CF010 | Wellpad TH26 (TH30) |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ |  |  |  |  | 590 | 699 | 770 | 770 |  |  | TH26-4.5.002-01 | 0300NDA10CF010 | CCI-DAT-1472 Note 2 |  | PRO-PID-0036 |  | bar(g) |  | 250 | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770
0300NDA10CF020 | Production Piping System | 10CF020 | Wellpad TH26 (TH30) |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 |  |  |  |  | 590 | 699 | 770 | 770 |  |  | 0 | 0300NDA10CF020 | CCI-DAT-1472 Note 2 |  | PRO-PID-0036 |  | bar(g) |  | 250 | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770
0300NDA10CP010 | Production Piping System | 10CP010 | Wellpad TH26 (TH30) |  | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 100 | 30 | -1 to 75 | 75 |  |  | TH26-4.5.002-01 | 0300NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0036 |  | °C |  | 250
0300NDA10CP510 | Production Piping System | 10CP510 | Wellpad TH26 (TH30) |  | Wika 72039884+14503369+0763349 |  |  |  |  | 100 | 30 | 100 | - |  |  | 0 | 0300NDA10CP510 | CCI-DAT-1460 |  | PRO-PID-0036 |  | °C |  | 250 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0300NDA10CP520 | Production Piping System | 10CP520 | Wellpad TH26 (TH30) |  | Wika 72039884+14503369+0763349 |  |  |  |  | 300 | 30 | 100 | - |  |  | 0 | 0300NDA10CP520 | CCI-DAT-1460 |  | PRO-PID-0036 |  | °C |  | 250 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0300NDA10CT010 | Production Piping System | 10CT010 | Wellpad TH26 (TH30) |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW |  |  |  |  | 60 | 235 | 300 | 300 |  |  | TH26-4.5.002-01 | 0300NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0036 |  | °C |  | 6000 | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300
0310NDB10CF010 | Separated Water System | 10CF010 | Wellpad TH29 (TH31) |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ |  |  |  |  | 60 | 150 | -5 to 200 | -5 to 200 |  |  | TH29-2.5.002-01 | 0310NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0032 |  | mm |  | 40
0310NDB10CP010 | Separated Water System | 10CP010 | Wellpad TH29 (TH31) |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 60 | 15 | -1 to 55 | 50 |  |  | TH29-2.5.002-01 | 0310NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0032 |  | bar(g) |  | 16
0310NDB10CP501 | Separated Water System | 10CP501 | Wellpad TH29 (TH31) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 60 | 15 | 60 | - |  |  | 0 | 0310NDB10CP501 | CCI-DAT-1460 |  | PRO-PID-0032 |  | °C |  | 60 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0310NDB10CP520 | Separated Water System | 10CP520 | Wellpad TH29 (TH31) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 60 | 15 | 60 | - |  |  | 0 | 0310NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-0032 |  | °C |  | 250 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0320NDB10CP501 | Separated Water System | 10CP501 | Wellpad LCP (LCP2-1) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 60 | 15 | 60 | - |  |  | 0 | 0320NDB10CP501 | CCI-DAT-1460 |  | PRO-PID-0038 |  | °C |  | 60 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0320NDB10CP520 | Separated Water System | 10CP520 | Wellpad LCP (LCP2-1) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 60 | 15 | 60 | - |  |  | 0 | 0320NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-0038 |  | °C |  | 25 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0330NDB10CP510 | Separated Water System | 10CP510 | Wellpad LCP (LCP2-2) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 60 | 15 | 60 | - |  |  | 0 | 0330NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-0038 |  | bar(g) |  | 15 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0330NDB10CP520 | Separated Water System | 10CP520 | Wellpad LCP (LCP2-2) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 40 | 15 | 60 | - |  |  | 0 | 0330NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-0038 |  | bar(g) |  | 15 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0340NDA10CF010 | Production Piping System | 10CF010 | Wellpad TH28 (TH34) |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ |  |  |  |  | 250 | 531 | 590 | 590 |  |  | TH28-9.5.002-01 | 0340NDA10CF010 | CCI-DAT-1472 Note 2 |  | PRO-PID-0031 |  | bar(g) |  | 15 | MVar1: 0; MVar2: 147.5; MVar3: 295; MVar4: 442.5; MVar5: 590
0340NDA10CF020 | Production Piping System | 10CF020 | Wellpad TH28 (TH34) |  | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 |  |  |  |  | 250 | 531 | 590 | 590 |  |  | 0 | 0340NDA10CF020 | CCI-DAT-1472 Note 2 |  | PRO-PID-0031 |  | bar(g) |  | 250 | MVar1: 0; MVar2: 147.5; MVar3: 295; MVar4: 442.5; MVar5: 590
0340NDA10CP010 | Production Piping System | 10CP010 | Wellpad TH28 (TH34) |  | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 26.3 | -1 to 75 | 75 |  |  | TH28-9.5.002-01 | 0340NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0031 |  | °C |  | 10
0340NDA10CP510 | Production Piping System | 10CP510 | Wellpad TH28 (TH34) |  | Wika 72039884+14503369+0763349 |  |  |  |  | 250 | 26.3 | 100 | - |  |  | 0 | 0340NDA10CP510 | CCI-DAT-1460 |  | PRO-PID-0031 |  | mm |  | 10 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0340NDA10CP520 | Production Piping System | 10CP520 | Wellpad TH28 (TH34) |  | Wika 72039884+14503369+0763349 |  |  |  |  | 250 | 20.5 | 100 | - |  |  | 0 | 0340NDA10CP520 | CCI-DAT-1460 |  | PRO-PID-0031 |  | mm |  | 10 | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100
0340NDA10CT010 | Production Piping System | 10CT010 | Wellpad TH28 (TH34) |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW |  |  |  |  | 250 | 216 | 300 | 300 |  |  | TH28-9.5.002-01 | 0340NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0031 |  | mm |  | 10 | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300
0350NDB10CF010 | Separated Water System | 10CF010 | Wellpad TH29 (TH35) |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ |  |  |  |  | 250 | 15 | -5 to 200 | -5 to 200 |  |  | 0 | 0350NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0032 |  | bar(g) |  | 10
0350NDB10CP010 | Separated Water System | 10CP010 | Wellpad TH29 (TEA-3) |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 30 | -1 to 55 | 50 |  |  | 0 | 0350NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0032 |  | bar(g) |  | 10
0350NDB10CP510 | Separated Water System | 10CP510 | Wellpad TH29 (TH35) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 6000 | 30 | 60 | - |  |  | 0 | 0350NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-0032 |  | bar(g) |  | 10 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0350NDB10CP520 | Separated Water System | 10CP520 | Wellpad TH29 (TH35) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 40 | 15 | 60 | - |  |  | 0 | 0350NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-0032 |  | bar(g) |  | 15 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
0370NDB10CF010 | Separated Water System | 10CF010 | Wellpad LCP (LCP2-1) |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ |  |  |  |  | 250 | 370 | -5 to 410 | -5 to 410 |  |  | TAS1-3.5.001-01 | 0370NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0038 |  | bar(g) |  | 15
0370NDB10CP010 | Separated Water System | 10CP010 | Wellpad LCP (LCP2-1) |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 15 | -1 to 55 | 50 |  |  | TAS1-3.5.001-01 | 0370NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0038 |  | bar(g) |  | 250
0380NDB10CF010 | Separated Water System | 10CF010 | Wellpad LCP (LCP2-2) |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ |  |  |  |  | 250 | 370 | -5 to 410 | -5 to 410 |  |  | TAS1-3.5.002-01 | 0380NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0038 |  | bar(g) |  | 250
0380NDB10CP010 | Separated Water System | 10CP010 | Wellpad LCP (LCP2-2) |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 15 | -1 to 55 | 50 |  |  | TAS1-3.5.002-01 | 0380NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0038 |  | bar(g) |  | 250
1910NDB10CF010 | Separated Water System | 10CF010 | Wellpad TH19N (TH19N_1) |  | Deleted Deleted |  |  |  |  | 250 | 370 | -5 to 410 | -5 to 410 |  |  | 0 | 1910NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0039 |  | bar(g) |  | 250
1910NDB10CP010 | Separated Water System | 10CP010 | Wellpad TH19N (TH19N_1) |  | Deleted Deleted |  |  |  |  | 250 | 15 | -1 to 55 | 50 |  |  | 0 | 1910NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0039 |  | bar(g) |  | 15
1910NDB10CP510 | Separated Water System | 10CP510 | Wellpad TH19N (TH19N_1) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 16 | 15 | 60 | - |  |  | 0 | 1910NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-0039 |  | bar(g) |  | 15 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
1910NDB10CP520 | Separated Water System | 10CP520 | Wellpad TH19N (TH19N_1) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 60 | 15 | 60 | - |  |  | 0 | 1910NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-0039 |  | bar(g) |  | 15 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
1920NDB10CF010 | Separated Water System | 10CF010 | Wellpad TH19N (TH19N_2) |  | Deleted Deleted |  |  |  |  | 250 | 370 | -5 to 410 | -5 to 410 |  |  | 0 | 1920NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0039 |  | bar(g) |  | 15
1920NDB10CP010 | Separated Water System | 10CP010 | Wellpad TH19N (TH19N_2) |  | Deleted Deleted |  |  |  |  | 60 | 15 | -1 to 55 | 50 |  |  | 0 | 1920NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0039 |  | bar(g) |  | 15
1920NDB10CP501 | Separated Water System | 10CP501 | Wellpad TH19N (TH19N_2) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 250 | 15 | 60 | - |  |  | 0 | 1920NDB10CP501 | CCI-DAT-1460 |  | PRO-PID-0039 |  | bar(g) |  | 1200 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
1920NDB10CP520 | Separated Water System | 10CP520 | Wellpad TH19N (TH19N_2) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 60 | 15 | 60 | - |  |  | 0 | 1920NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-0039 |  | bar(g) |  | 10000 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
1930NDB10CF010 | Separated Water System | 10CF010 | Wellpad TH19N (TH19N_3) |  | Deleted Deleted |  |  |  |  | 250 | 370 | -5 to 410 | -5 to 410 |  |  | 0 | 1930NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0039 |  | bar(g) |  | 10000
1930NDB10CP010 | Separated Water System | 10CP010 | Wellpad TH19N (TH19N_3) |  | Deleted Deleted |  |  |  |  | 6000 | 15 | -1 to 55 | 50 |  |  | 0 | 1930NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0039 |  | mm |  | 10000
1930NDB10CP510 | Separated Water System | 10CP510 | Wellpad TH19N (TH19N_3) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 25 | 15 | 60 | - |  |  | 0 | 1930NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-0039 |  | mm |  | 250 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
1930NDB10CP520 | Separated Water System | 10CP520 | Wellpad TH19N (TH19N_3) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 15 | 15 | 60 | - |  |  | 0 | 1930NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-0039 |  | mm |  | 150 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
L050NDA10CP010 | Production Piping System | 10CP010 | TH12 Two Phase Pipeline |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 15 | 21.27 | -1 to 55 | 35 |  |  | TAS2-205-01 | L050NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0011 |  | mm |  | 250
L050NDA10CP532 | Production Piping System | 10CP532 | TH12 Two Phase Pipeline |  | Wika 72039883+14503369+0763349 |  |  |  |  | 15 | 25 | 40 | - |  |  | 0 | L050NDA10CP532 | CCI-DAT-1460 |  | PRO-PID-0037 |  | mm |  | 1350 | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40
L050NDA10CT010 | Production Piping System | 10CT010 | TH12 Two Phase Pipeline |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW |  |  |  |  | 15 | 217.9 | 250 | 250 |  |  | TAS2-205-01 | L050NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0011 |  | mm |  | 1350 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L050NDA10CT030 | Production Piping System | 10CT030 | TH12 Two Phase Pipeline |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW |  |  |  |  | 250 | 215 | 250 | 250 |  |  | TH12-8.5.001-01 | L050NDA10CT030 | CCI-DAT-1465 |  | PRO-PID-0037 |  | mm |  | 1350 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L060NDA10CP010 | Production Piping System | 10CP010 | TH28 Two Phase Pipeline |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 15 | 21.27 | -1 to 55 | 35 |  |  | TAS2-105-01 | L060NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0011 |  | °C |  | 250
L060NDA10CP531 | Production Piping System | 10CP531 | TH28 Two Phase Pipeline |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 10 | 20.5 | -1 to 55 | 50 |  |  | 0 | L060NDA10CP531 | CCI-DAT-1461 |  | PRO-PID-0031 |  | °C |  | 10
L060NDA10CT010 | Production Piping System | 10CT010 | TH28 Two Phase Pipeline |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0370SLAR1C2B1UAE065TBXW+114CM0295TAC2SC075AQ5Q8R21XW |  |  |  |  | 10 | 217.9 | 250 | 250 |  |  | TAS2-105-01 | L060NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0011 |  | °C |  | 10 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L060NDA10CT030 | Production Piping System | 10CT030 | TH28 Two Phase Pipeline |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW |  |  |  |  | 10 | 216 | 250 | 250 |  |  | TH28-9.5.001-01 | L060NDA10CT030 | CCI-DAT-1465 |  | PRO-PID-0031 |  | °C |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L060NDA10CT510 | Production Piping System | 10CT510 | TH28 Two Phase Pipeline |  | Wika 72039934+72039931 |  |  |  |  | 10 | 215 | 250 | - |  |  | 0 | L060NDA10CT510 | CCI-DAT-1463 |  | PRO-PID-0034 |  | °C |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L060NDA10CT511 | Production Piping System | 10CT511 | TH28 Two Phase Pipeline |  | Wika 72039935+72039932 |  |  |  |  | 10 | 215 | 250 | - |  |  | 0 | L060NDA10CT511 | CCI-DAT-1463 |  | PRO-PID-0034 |  | °C |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L060NDA10CT520 | Production Piping System | 10CT520 | TH28 Two Phase Pipeline |  | Wika 72039934+72039931 |  |  |  |  | 10 | 215 | 250 | - |  |  | 0 | L060NDA10CT520 | CCI-DAT-1463 |  | PRO-PID-0034 |  | °C |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L060NDA10CT521 | Production Piping System | 10CT521 | TH28 Two Phase Pipeline |  | Wika 72040072+72040071 |  |  |  |  | 10 | 215 | 250 | - |  |  | 0 | L060NDA10CT521 | CCI-DAT-1463 |  | PRO-PID-0034 |  | °C |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L070LFC10CL010 | Common Steam/Water Dump System | 10CL010 | TH26 Two Phase Pipeline |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 10 | - | 6000 | 6000 |  |  | TH28-9.5.001-01 | L070LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-0034 |  | °C |  | 250 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
L070NDA10CP010 | Production Piping System | 10CP010 | TH26 Two Phase Pipeline |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 15 | 21.27 | -1 to 55 | 35 |  |  | TAS2-105-01 | L070NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0011 |  | °C |  | 250
L070NDA10CP532 | Production Piping System | 10CP532 | TH26 Two Phase Pipeline |  | Wika 72039883+14503369+0763349 |  |  |  |  | 15 | 25 | 40 | - |  |  | 0 | L070NDA10CP532 | CCI-DAT-1460 |  | PRO-PID-0036 |  | mm/s |  | 250 | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40
L070NDA10CT010 | Production Piping System | 10CT010 | TH26 Two Phase Pipeline |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0370SLAR1C2B1UAE065TBXW+114CM0295TAC2SC075AQ5Q8R21XW |  |  |  |  | 15 | 217.9 | 250 | 250 |  |  | TAS2-105-01 | L070NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0011 |  | mm/s |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L070NDA10CT030 | Production Piping System | 10CT030 | TH26 Two Phase Pipeline |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW |  |  |  |  | 250 | 215 | 250 | 250 |  |  | TH26-4.5.001-01 | L070NDA10CT030 | CCI-DAT-1465 |  | PRO-PID-0036 |  | mm/s |  | 20 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L070NDA10-CT510 | Production Piping System | 10-CT510 | TH26 Two Phase Pipeline |  | Wika 72039934+72039931 |  |  |  |  | 250 | 215 | 250 | - |  |  | TH26-4.5.001-01 | L070NDA10-CT510 | CCI-DAT-1463 |  | PRO-PID-0034 |  | mm/s |  | 2500 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L070NDA10CT511 | Production Piping System | 10CT511 | TH26 Two Phase Pipeline |  | Wika 72039934+72039931 |  |  |  |  | 250 | 215 | 250 | - |  |  | 0 | L070NDA10CT511 | CCI-DAT-1463 |  | PRO-PID-0034 |  | mm/s |  | 1000 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L070NDA10CT512 | Production Piping System | 10CT512 | TH26 Two Phase Pipeline |  | Wika 72039935+72039932 |  |  |  |  | 250 | 215 | 250 | - |  |  | 0 | L070NDA10CT512 | CCI-DAT-1463 |  | PRO-PID-0034 |  | mm/s |  | 2500 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L070NDA10CT522 | Production Piping System | 10CT522 | TH26 Two Phase Pipeline |  | Wika 72040072+72040071 |  |  |  |  | 15 | 215 | 250 | - |  |  | 0 | L070NDA10CT522 | CCI-DAT-1463 |  | PRO-PID-0034 |  | °C |  | 2 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L150NAB10CP510 | Condensate System | 10CP510 | Condensate Pipeline To TH11 |  | Wika 72039879+14503369+0731277 |  |  |  |  | 15 | 5 | 16 | - |  |  | 0 | L150NAB10CP510 | CCI-DAT-1460 |  | PRO-PID-0033 |  | °C |  | 2 | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16
L190NDB10CP010 | Separated Water System | 10CP010 | SGW Pipeline To TH29 Well Pad |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 15 | 30 | -1 to 55 | -1 to 50 |  |  | TAS1-3.5.002-01 | L190NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0035 |  | °C |  | 2
L190NDB10CP011 | Separated Water System | 10CP011 | SWG Pipeline to TH29 Wellpad |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 15 | 15 | -1 to 55 | 50 |  |  | TH29-2.5.001-01 | L190NDB10CP011 | CCI-DAT-1461 |  | PRO-PID-0032 |  | °C |  | 4
L190NDB10CP510 | Separated Water System | 10CP510 | SWG Pipeline to TH29 Wellpad |  | Wika 72039876+14503369+0731277 |  |  |  |  | 15 | 15 | 60 | - |  |  | 0 | L190NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-0032 |  | °C |  | 3 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
L190NDB10CT010 | Separated Water System | 10CT010 | SWG Pipeline to TH29 Wellpad |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW |  |  |  |  | 15 | 123 | 250 | 150 |  |  | TH29-2.5.001-01 | L190NDB10CT010 | CCI-DAT-1465 |  | PRO-PID-0032 |  | mm/s |  | 25 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L200NDB10CP010 | Separated Water System | 10CP010 | SGW Pipeline To TH19N |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 15 | 30 | -1 to 55 | -1 to 50 |  |  | TAS1-3.5.002-01 | L200NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0035 |  | mm/s |  | 5
L210NDB10CP011 | Separated Water System | 10CP011 | SWG Pipeline to TH29 Wellpad |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 15 | 15 | -1 to 55 | 50 |  |  | 0 | L210NDB10CP011 | CCI-DAT-1461 |  | PRO-PID-0032 |  | mm/s |  | 2
L210NDB10CP510 | Separated Water System | 10CP510 | SGW Pipeline To Wellpad LCP |  | Wika 72039876+14503369+0731277 |  |  |  |  | 15 | 15 | 60 | - |  |  | 0 | L210NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-0038 |  | mbar(g) |  | 2 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
L210NDB10CT010 | Separated Water System | 10CT010 | SGW Pipeline To Wellpad LCP |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW |  |  |  |  | 1200 | 123 | 250 | 150 |  |  | TAS1-3.5.001-01 | L210NDB10CT010 | CCI-DAT-1465 |  | PRO-PID-0038 |  | mbar(g) |  | 2 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
L220NDB10CP510 | Separated Water System | 10CP510 | Wellpad TH19N (TH19N_1) |  | Wika 72039876+14503369+0731277 |  |  |  |  | 10000 | 15 | 60 | - |  |  | 0 | L220NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-0039 |  | mbar(g) |  | 60 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
L220NDB10CT010 | Separated Water System | 10CT010 | Wellpad TH19N (TH19N_1) |  | Deleted Deleted |  |  |  |  | 10000 | 123 | 250 | 150 |  |  | 0 | L220NDB10CT010 | CCI-DAT-1465 |  | PRO-PID-0039 |  | bar(g) |  | 60 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
LCP0LFC10CL010 | Common Steam/Water Dump System | 10CL010 | Wellpad LCP |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 10000 | - | 6000 | 6000 |  |  | 0 | LCP0LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-0038 |  | bar(g) |  | 60 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
P020GAC20CL010 | Seal Water System | 20CL010 | Pump Station |  | Rosemount 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8+751AM1NAB+ |  |  |  |  | 6000 | N/A | Note 9 | Note 9 |  |  | 0 | P020GAC20CL010 | CCI-DAT-1468 |  | PRO-PID-0041 |  | bar(g) |  | 60
P020GAC20CL011 | Seal Water System | 20CL011 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 6000 | N/A | Note 9 | Refer to Notes |  |  | 0 | P020GAC20CL011 | CCI-DAT-1471 |  | PRO-PID-0041 |  | bar(g) |  | 3125
P020GAC20CL020 | Seal Water System | 20CL020 | Pump Station |  | Rosemount 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8+751AM1NAB+ |  |  |  |  | 6000 | N/A | Note 9 | Note 9 |  |  | 0 | P020GAC20CL020 | CCI-DAT-1468 |  | PRO-PID-0041 |  | bar(g) |  | 3125
P020GAC20CL021 | Seal Water System | 20CL021 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 6000 | N/A | Note 9 | Refer to Notes |  |  | 0 | P020GAC20CL021 | CCI-DAT-1471 |  | PRO-PID-0041 |  | bar(g) |  | 3125
P020GAC20CP020 | Raw Water System | 20CP020 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 3.49 | 25 | - |  |  | 0 | P020GAC20CP020 | CCI-DAT-1460 |  | PRO-PID-0051 |  | °C |  | 250 | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25
P020GAC20CP510 | Seal Water System | 20CP510 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 150 | 11.77 | 15 | - |  |  | 0 | P020GAC20CP510 | CCI-DAT-1460 |  | PRO-PID-0041 |  | °C |  | 250 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GAC20CP511 | Seal Water System | 20CP511 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 250 | 11.77 | 15 | - |  |  | 0 | P020GAC20CP511 | CCI-DAT-1460 |  | PRO-PID-0041 |  | °C |  | 250 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GAC30CP590 | Seal Water System | 30CP590 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 1350 | 11.77 | 15 | - |  |  | 0 | P020GAC30CP590 | CCI-DAT-1460 |  | PRO-PID-0041 |  | °C |  | 250 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GAC30CP591 | Seal Water System | 30CP591 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 1350 | 11.77 | 15 | - |  |  | 0 | P020GAC30CP591 | CCI-DAT-1460 |  | PRO-PID-0041 |  | °C |  | 1200 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GAC30CT050 | Seal Water System | 30CT050 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW |  |  |  |  | 1350 | 32 | 250 | - |  |  | 0 | P020GAC30CT050 | CCI-DAT-1466 |  | PRO-PID-0041 |  | °C |  | 20 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020GWA20CL010 | VSD Cooling Water System | 20CL010 | Pump Station |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 |  |  |  |  | 500 | 773 | TBC | TBC |  |  | TAS3 101-05 | P020GWA20CL010 | CCI-DAT-1467 |  | PRO-PID-0044 |  | °C |  | 60
P020GWA21CP001 | Seal Water System | 21CP001 | Pump Station |  | Rosemount 2051CD3A02A1BS5M4Q4 c/w 0305RC52B11B4++ |  |  |  |  | 500 | 0 | -2500 to 2500 | 250mbar |  |  | TAS3 207-01 | P020GWA21CP001 | CCI-DAT-1462 |  | PRO-PID-0042 |  | °C |  | 2680
P020GWA21CP002 | Seal Water System | 21CP002 | Pump Station |  | Rosemount 2051TG1A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 500 | -0.34 | -1 to 55 | -0.69 to -0.34 |  |  | TAS3 101-07 | P020GWA21CP002 | CCI-DAT-1461 |  | PRO-PID-0042 |  | °C |  | 2680
P020GWA22CP010 | Seal Water System | 22CP010 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 11.77 | -1 to 55 | 15 |  |  | TAS3 101-06 | P020GWA22CP010 | CCI-DAT-1461 |  | PRO-PID-0042 |  | °C |  | 2680
P020GWA22CP510 | Seal Water System | 22CP510 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 250 | 11.77 | 15 | - |  |  | 0 | P020GWA22CP510 | CCI-DAT-1460 |  | PRO-PID-0042 |  | °C |  | 25 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA23CP020 | Seal Water System | 23CP020 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 11.77 | -1 to 55 | 15 |  |  | TAS3 101-07 | P020GWA23CP020 | CCI-DAT-1461 |  | PRO-PID-0042 |  | °C |  | 14
P020GWA24CP030 | Seal Water System | 24CP030 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 10 | 11.77 | -1 to 55 | 15 |  |  | TAS3 207-01 | P020GWA24CP030 | CCI-DAT-1461 |  | PRO-PID-0042 |  | °C |  | 40
P020GWA30CF010 | Seal Water System | 30CF010 | Pump Station |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 10 | 8 | 10 | 10 |  |  | TAS3 101-08 | P020GWA30CF010 | CCI-DAT-1474 |  | PRO-PID-0043 |  | °C |  | 5 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020GWA30CF011 | Seal Water System | 30CF011 | Pump Station |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 10 | 8 | 10 | 10 |  |  | TAS3 101-08 | P020GWA30CF011 | CCI-DAT-1474 |  | PRO-PID-0043 |  | °C |  | 40 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020GWA30CF020 | Seal Water System | 30CF020 | Pump Station |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 250 | 8 | 10 | 10 |  |  | 0 | P020GWA30CF020 | CCI-DAT-1474 |  | PRO-PID-0043 |  | mm/s |  | 1500 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020GWA30CF021 | Seal Water System | 30CF021 | Pump Station |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 250 | 8 | 10 | 10 |  |  | 0 | P020GWA30CF021 | CCI-DAT-1474 |  | PRO-PID-0043 |  | mm/s |  | 1500 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020GWA30CF030 | Seal Water System | 30CF030 | Pump Station |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 250 | 8 | 10 | 10 |  |  | 0 | P020GWA30CF030 | CCI-DAT-1474 |  | PRO-PID-0043 |  | mm/s |  | 16 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020GWA30CF031 | Seal Water System | 30CF031 | Pump Station |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 250 | 8 | 10 | 10 |  |  | 0 | P020GWA30CF031 | CCI-DAT-1474 |  | PRO-PID-0043 |  | mm/s |  | 16 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020GWA30CF040 | Seal Water System | 30CF040 | Pump Station |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 250 | 8 | 10 | 10 |  |  | 0 | P020GWA30CF040 | CCI-DAT-1474 |  | PRO-PID-0043 |  | mm/s |  | 16 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020GWA30CF041 | Seal Water System | 30CF041 | Pump Station |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 250 | 8 | 10 | 10 |  |  | 0 | P020GWA30CF041 | CCI-DAT-1474 |  | PRO-PID-0043 |  | mm/s |  | 16 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020GWA30CP501 | Seal Water System | 30CP501 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 250 | 11.77 | 15 | - |  |  | 0 | P020GWA30CP501 | CCI-DAT-1460 |  | PRO-PID-0043 |  | mm/s |  | 250 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA30CP502 | Seal Water System | 30CP502 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 250 | 11.77 | 15 | - |  |  | 0 | P020GWA30CP502 | CCI-DAT-1460 |  | PRO-PID-0043 |  | mm/s |  | 250 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA30CP503 | Seal Water System | 30CP503 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 250 | 11.77 | 15 | - |  |  | 0 | P020GWA30CP503 | CCI-DAT-1460 |  | PRO-PID-0043 |  | mm/s |  | 250 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA30CT010 | Seal Water System | 30CT010 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW |  |  |  |  | 20 | 32 | 250 | 100 |  |  | TAS3 101-01 | P020GWA30CT010 | CCI-DAT-1465 |  | PRO-PID-0043 |  | mm/s |  | 20 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020GWA30CT020 | Seal Water System | 30CT020 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW |  |  |  |  | 2500 | 32 | 250 | 100 |  |  | 0 | P020GWA30CT020 | CCI-DAT-1465 |  | PRO-PID-0043 |  | mm/s |  | 2500 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020GWA30CT030 | Seal Water System | 30CT030 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW |  |  |  |  | 1000 | 32 | 250 | 100 |  |  | 0 | P020GWA30CT030 | CCI-DAT-1465 |  | PRO-PID-0043 |  | mm/s |  | 1000 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020GWA30CT040 | Seal Water System | 30CT040 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW |  |  |  |  | 2500 | 32 | 250 | 100 |  |  | 0 | P020GWA30CT040 | CCI-DAT-1465 |  | PRO-PID-0043 |  | mm/s |  | 2500 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020GWA31CP511 | Seal Water System | 31CP511 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 2 | 11.77 | 15 | - |  |  | 0 | P020GWA31CP511 | CCI-DAT-1460 |  | PRO-PID-0043 |  | mm/s |  | 2 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA31CP512 | Seal Water System | 31CP512 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 2 | 11.77 | 15 | - |  |  | 0 | P020GWA31CP512 | CCI-DAT-1460 |  | PRO-PID-0043 |  | mm/s |  | 2 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA31CP513 | Seal Water System | 31CP513 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 2 | 11.77 | 15 | - |  |  | 0 | P020GWA31CP513 | CCI-DAT-1460 |  | PRO-PID-0043 |  | bar(g) |  | 2 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA32CP521 | Seal Water System | 32CP521 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 4 | 11.77 | 15 | - |  |  | 0 | P020GWA32CP521 | CCI-DAT-1460 |  | PRO-PID-0043 |  | bar(g) |  | 4 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA32CP522 | Seal Water System | 32CP522 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 3 | 11.77 | 15 | - |  |  | 0 | P020GWA32CP522 | CCI-DAT-1460 |  | PRO-PID-0043 |  | bar(g) |  | 3 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA32CP523 | Seal Water System | 32CP523 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 25 | 11.77 | 15 | - |  |  | 0 | P020GWA32CP523 | CCI-DAT-1460 |  | PRO-PID-0043 |  | mm |  | 25 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA33CP531 | Seal Water System | 33CP531 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 5 | 11.77 | 15 | - |  |  | 0 | P020GWA33CP531 | CCI-DAT-1460 |  | PRO-PID-0043 |  | mm |  | 5 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA33CP532 | Seal Water System | 33CP532 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 2 | 11.77 | 15 | - |  |  | 0 | P020GWA33CP532 | CCI-DAT-1460 |  | PRO-PID-0043 |  | l/m |  | 2 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020GWA33CP533 | Seal Water System | 33CP533 | Pump Station |  | Wika 72039876+14503369+ |  |  |  |  | 2 | 11.77 | 15 | - |  |  | 0 | P020GWA33CP533 | CCI-DAT-1460 |  | PRO-PID-0043 |  | l/m |  | 2 | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15
P020LFC20CF010 | Common Steam/Water Dump System | 20CF010 | Pump Station |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P200A3SC065Q8+ |  |  |  |  | 2 | 1120 | 1200 | 1200 |  |  | TAS3 206-01 | P020LFC20CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0028 |  | l/m |  | 2 | MVar1: 0; MVar2: 300; MVar3: 600; MVar4: 900; MVar5: 1200
P020LFC20CL001 | Common Steam/Water Dump System | 20CL001 | Pump Station |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 60 | N/A | 10000 | 10000 |  |  | TAS3 101-06 | P020LFC20CL001 | CCI-DAT-1468 |  | PRO-PID-0028 |  | l/m |  | 60 | MVar1: 0; MVar2: 2500; MVar3: 5000; MVar4: 7500; MVar5: 10000
P020LFC20CL002 | Common Steam/Water Dump System | 20CL002 | Pump Station |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 60 | N/A | 10000 | 10000 |  |  | TAS3 206-01 | P020LFC20CL002 | CCI-DAT-1468 |  | PRO-PID-0028 |  | l/m |  | 60 | MVar1: 0; MVar2: 2500; MVar3: 5000; MVar4: 7500; MVar5: 10000
P020LFC20CL003 | Common Steam/Water Dump System | 20CL003 | Pump Station |  | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX |  |  |  |  | 60 | N/A | 10000 | 10000 |  |  | TAS3 101-09 | P020LFC20CL003 | CCI-DAT-1468 |  | PRO-PID-0028 |  | l/m |  | 60 | MVar1: 0; MVar2: 2500; MVar3: 5000; MVar4: 7500; MVar5: 10000
P020LFC20CL010 | Common Steam/Water Dump System | 20CL010 | Pump Station |  | Vega B86.IXCMAXAGDHXATMKM |  |  |  |  | 60 | 0 | 6000 | 6000 |  |  | TAS3 101-06 | P020LFC20CL010 | CCI-DAT-1480 |  | PRO-PID-0028 |  | mm |  | 60 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
P020LFC20CL020 | Common Steam/Water Dump System | 20CL020 | Pump Station |  | Vega B86.IXCMAXAGDHXATMKM |  |  |  |  | 3125 | 0 | 6000 | 6000 |  |  | TAS3 101-07 | P020LFC20CL020 | CCI-DAT-1480 |  | PRO-PID-0028 |  | mm |  | 3125 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
P020LFC20CL030 | Common Steam/Water Dump System | 20CL030 | Pump Station |  | Vega B86.IXCMAXAGDHXATMKM |  |  |  |  | 3125 | 0 | 6000 | 6000 |  |  | TAS3 206-01 | P020LFC20CL030 | CCI-DAT-1480 |  | PRO-PID-0028 |  | mm |  | 3125 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
P020LFC20CL040 | Common Steam/Water Dump System | 20CL040 | Pump Station |  | Vega B86.IXCMAXAGDHXATMKM |  |  |  |  | 3125 | 0 | 6000 | 6000 |  |  | TAS3 207-01 | P020LFC20CL040 | CCI-DAT-1480 |  | PRO-PID-0028 |  | - |  | 3125 | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000
P020LFC20CP010 | Common Steam/Water Dump System | 20CP010 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 3125 | 16 | -1 to 55 | 25 |  |  | TAS3 101-06 | P020LFC20CP010 | CCI-DAT-1461 |  | PRO-PID-0028 |  | mm |  | 3125
P020LFC20CT011 | Common Steam/Water Dump System | 20CT011 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+Wika Submersible Sensor+ |  |  |  |  | 250 | 45 | 250 | 100 |  |  | TAS3 201-01 | P020LFC20CT011 | CCI-DAT-1465 |  | PRO-PID-0028 |  | mm |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020LFC20CT012 | Common Steam/Water Dump System | 20CT012 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT012 | PRO-DAT-0022 |  | PRO-PID-0028 |  | kg/s |  | 250
P020LFC20CT013 | Common Steam/Water Dump System | 20CT013 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT013 | PRO-DAT-0022 |  | PRO-PID-0028 |  | kg/s |  | 250
P020LFC20CT014 | Common Steam/Water Dump System | 20CT014 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT014 | PRO-DAT-0022 |  | PRO-PID-0028 |  | kg/s |  | 250
P020LFC20CT015 | Common Steam/Water Dump System | 20CT015 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT015 | PRO-DAT-0022 |  | PRO-PID-0028 |  | kg/s |  | 250
P020LFC20CT016 | Common Steam/Water Dump System | 20CT016 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT016 | PRO-DAT-0022 |  | PRO-PID-0028 |  | kg/s |  | 250
P020LFC20CT022 | Common Steam/Water Dump System | 20CT022 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT022 | PRO-DAT-0022 |  | PRO-PID-0028 |  | bar(g) |  | 250
P020LFC20CT023 | Common Steam/Water Dump System | 20CT023 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT023 | PRO-DAT-0022 |  | PRO-PID-0028 |  | bar(g) |  | 250
P020LFC20CT024 | Common Steam/Water Dump System | 20CT024 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT024 | PRO-DAT-0022 |  | PRO-PID-0028 |  | bar(g) |  | 250
P020LFC20CT025 | Common Steam/Water Dump System | 20CT025 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT025 | PRO-DAT-0022 |  | PRO-PID-0028 |  | bar(g) |  | 250
P020LFC20CT026 | Common Steam/Water Dump System | 20CT026 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CT026 | PRO-DAT-0022 |  | PRO-PID-0028 |  | bar(g) |  | 250
P020LFC20CY010 | Common Steam/Water Dump System | 20CY010 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CY010 | PRO-DAT-0022 |  | PRO-PID-0028 |  | mm |  | 250
P020LFC20CY011 | Common Steam/Water Dump System | 20CY011 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CY011 | PRO-DAT-0022 |  | PRO-PID-0028 |  | mm |  | 250
P020LFC20CY012 | Common Steam/Water Dump System | 20CY012 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CY012 | PRO-DAT-0022 |  | PRO-PID-0028 |  | mm |  | 250
P020LFC20CY020 | Common Steam/Water Dump System | 20CY020 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CY020 | PRO-DAT-0022 |  | PRO-PID-0028 |  | mm |  | 250
P020LFC20CY021 | Common Steam/Water Dump System | 20CY021 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CY021 | PRO-DAT-0022 |  | PRO-PID-0028 |  | kg/s |  | 250
P020LFC20CY022 | Common Steam/Water Dump System | 20CY022 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020LFC20CY022 | PRO-DAT-0022 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CF010 | Condensate System | 10CF010 | Pump Station |  | Rosemount 8750WDMT2A2FNSA120CA1M4Q4Q8+Included in Flowtube Model+ |  |  |  |  | 250 | 455 | 150 | 600 |  |  | TAS3 101-06 | P020NAB10CF010 | CCI-DAT-1474 |  | PRO-PID-0028 |  | mm |  | 250 | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150
P020NAB10CP010 | Condensate System | 10CP010 | Pump Station |  | Rosemount 2051CD3A02A1BS5M4Q4 c/w 0305RC52B11B4++ |  |  |  |  | 250 | 0 | -2500 to 2500 | 250mbar |  |  | TAS3 101-06 | P020NAB10CP010 | CCI-DAT-1462 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CP011 | Condensate System | 10CP011 | Pump Station |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 0.8 | -1 to 55 | 3 |  |  | TAS3 101-06 | P020NAB10CP011 | CCI-DAT-1461 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CP012 | Condensate System | 10CP012 | Pump Station |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 3.5 | -1 to 55 | 10 |  |  | TAS3 101-06 | P020NAB10CP012 | CCI-DAT-1461 |  | PRO-PID-0028 |  | kg/s |  | 250
P020NAB10CP030 | Condensate System | 10CP030 | Pump Station |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 250 | 3.5 | -1 to 55 | 10 |  |  | TAS3 206-01 | P020NAB10CP030 | CCI-DAT-1461 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CT012 | Condensate System | 10CT012 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NAB10CT012 | PRO-DAT-0021 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CT013 | Condensate System | 10CT013 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NAB10CT013 | PRO-DAT-0021 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CT014 | Condensate System | 10CT014 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NAB10CT014 | PRO-DAT-0021 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CT015 | Condensate System | 10CT015 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NAB10CT015 | PRO-DAT-0021 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CT016 | Condensate System | 10CT016 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NAB10CT016 | PRO-DAT-0021 |  | PRO-PID-0028 |  | kg/s |  | 250
P020NAB10CT030 | Condensate System | 10CT030 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW |  |  |  |  | 250 | 45 | 250 | - |  |  | TAS3 101-02 | P020NAB10CT030 | CCI-DAT-1466 |  | PRO-PID-0028 |  | mm |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020NAB10CY010 | Condensate System | 10CY010 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NAB10CY010 | PRO-DAT-0021 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CY011 | Condensate System | 10CY011 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NAB10CY011 | PRO-DAT-0021 |  | PRO-PID-0028 |  | mm |  | 250
P020NAB10CY012 | Condensate System | 10CY012 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NAB10CY012 | PRO-DAT-0021 |  | PRO-PID-0028 |  | mm |  | 250
P020NDB10CF010 | Separated Water System | 10CF010 | Pump Station |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A6SC065Q8+ |  |  |  |  | 250 | 1135 | 1350 | 1350 |  |  | TAS3 101-04 | P020NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0026 |  | mm |  | 0 | MVar1: 0; MVar2: 337.5; MVar3: 675; MVar4: 1012.5; MVar5: 1350
P020NDB10CF020 | Separated Water System | 10CF020 | Pump Station |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A6SC065Q8+ |  |  |  |  | 1200 | 1135 | 1350 | 1350 |  |  | TAS3 206-01 | P020NDB10CF020 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0026 |  | kg/s |  | 1350 | MVar1: 0; MVar2: 337.5; MVar3: 675; MVar4: 1012.5; MVar5: 1350
P020NDB10CF030 | Separated Water System | 10CF030 | Pump Station |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A6SC065Q8+ |  |  |  |  | 20 | 1135 | 1350 | 1350 |  |  | TAS3 205-01 | P020NDB10CF030 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0026 |  | mm |  | 1350 | MVar1: 0; MVar2: 337.5; MVar3: 675; MVar4: 1012.5; MVar5: 1350
P020NDB10CP011 | Separated Water System | 10CP011 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 60 | 35 | -1 to 55 | 45 |  |  | TAS3 101-04 | P020NDB10CP011 | CCI-DAT-1461 |  | PRO-PID-0026 |  | mm |  | 500
P020NDB10CP014 | Separated Water System | 10CP014 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 60 | 35 | -1 to 55 | 45 |  |  | TAS3 204-01 | P020NDB10CP014 | CCI-DAT-1461 |  | PRO-PID-0026 |  | mm |  | 500
P020NDB10CP015 | Separated Water System | 10CP015 | Pump Station |  | Wika 72039917++11585791 |  |  |  |  | 60 | 0 | 500 | - |  |  | 0 | P020NDB10CP015 | CCI-DAT-1462 |  | PRO-PID-0026 |  | mm |  | 500 | MVar1: 0; MVar2: 125; MVar3: 250; MVar4: 375; MVar5: 500
P020NDB10CP021 | Separated Water System | 10CP021 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 2680 | 35 | -1 to 55 | 45 |  |  | TAS3 101-05 | P020NDB10CP021 | CCI-DAT-1461 |  | PRO-PID-0026 |  | mm |  | 250
P020NDB10CP024 | Separated Water System | 10CP024 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 2680 | 35 | -1 to 55 | 45 |  |  | TAS3 206-01 | P020NDB10CP024 | CCI-DAT-1461 |  | PRO-PID-0026 |  | mm |  | 250
P020NDB10CP025 | Separated Water System | 10CP025 | Pump Station |  | Wika 72039917++11585791 |  |  |  |  | 2680 | 0 | 500 | . |  |  | 0 | P020NDB10CP025 | CCI-DAT-1462 |  | PRO-PID-0026 |  | mm |  | 250 | MVar1: 0; MVar2: 0.25; MVar3: 0.5; MVar4: 0.75; MVar5: 1
P020NDB10CP031 | Separated Water System | 10CP031 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 5690 | 35 | -1 to 55 | 45 |  |  | TAS3 101-09 | P020NDB10CP031 | CCI-DAT-1461 |  | PRO-PID-0026 |  | mm/Time Unit |  | 10
P020NDB10CP034 | Separated Water System | 10CP034 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 2680 | 35 | -1 to 55 | 45 |  |  | TAS3 205-01 | P020NDB10CP034 | CCI-DAT-1461 |  | PRO-PID-0026 |  | mm/Time Unit |  | 10
P020NDB10CP035 | Separated Water System | 10CP035 | Pump Station |  | Wika 72039917++11585791 |  |  |  |  | 2680 | 0 | 500 | - |  |  | 0 | P020NDB10CP035 | CCI-DAT-1462 |  | PRO-PID-0026 |  | mm/Time Unit |  | 10 | MVar1: 0; MVar2: 125; MVar3: 250; MVar4: 375; MVar5: 500
P020NDB10CP040 | Separated Water System | 10CP040 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 2680 | 35 | -1 to 55 | 45 |  |  | TAS3 204-01 | P020NDB10CP040 | CCI-DAT-1461 |  | PRO-PID-0026 |  | mm/Time Unit |  | 250
P020NDB10CP512 | Separated Water System | 10CP512 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | 35 | See Notes | - |  |  | 0 | P020NDB10CP512 | PRO-DAT-0020 CCI-DAT-1460 |  | PRO-PID-0026 |  | bar(g) |  | 250
P020NDB10CP513 | Separated Water System | 10CP513 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | 35 | See Notes | - |  |  | 0 | P020NDB10CP513 | PRO-DAT-0020 CCI-DAT-1460 |  | PRO-PID-0026 |  | pH |  | 250
P020NDB10CP522 | Separated Water System | 10CP522 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | 35 | See Notes | - |  |  | 0 | P020NDB10CP522 | PRO-DAT-0020 CCI-DAT-1460 |  | PRO-PID-0026 |  | bar(g) |  | 250
P020NDB10CP523 | Separated Water System | 10CP523 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 900 | 35 | See Notes | - |  |  | 0 | P020NDB10CP523 | PRO-DAT-0020 CCI-DAT-1460 |  | PRO-PID-0026 |  | pH |  | 250
P020NDB10CP532 | Separated Water System | 10CP532 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 900 | 35 | See Notes | - |  |  | 0 | P020NDB10CP532 | PRO-DAT-0020 CCI-DAT-1460 |  | PRO-PID-0026 |  | mm |  | 250
P020NDB10CP533 | Separated Water System | 10CP533 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | 35 | See Notes | - |  |  | 0 | P020NDB10CP533 | PRO-DAT-0020 CCI-DAT-1460 |  | PRO-PID-0026 |  | pH |  | 250
P020NDB10CT010 | Separated Water System | 10CT010 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW |  |  |  |  | 2680 | 123 | 250 | - |  |  | TAS3 101-01 | P020NDB10CT010 | CCI-DAT-1466 |  | PRO-PID-0026 |  | pH |  | 250 | MVar1: 0; MVar2: 0.25; MVar3: 0.5; MVar4: 0.75; MVar5: 1
P020NDB10CT013 | Separated Water System | 10CT013 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT013 | PRO-DAT-0020 |  | PRO-PID-0026 |  | pH |  | 250
P020NDB10CT014 | Separated Water System | 10CT014 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 5440 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT014 | PRO-DAT-0020 |  | PRO-PID-0026 |  | pH |  | 20
P020NDB10CT015 | Separated Water System | 10CT015 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT015 | PRO-DAT-0020 |  | PRO-PID-0026 |  | mm |  | 2500
P020NDB10CT016 | Separated Water System | 10CT016 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT016 | PRO-DAT-0020 |  | PRO-PID-0026 |  | mm |  | 1000
P020NDB10CT017 | Separated Water System | 10CT017 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT017 | PRO-DAT-0020 |  | PRO-PID-0026 |  | mm |  | 2500
P020NDB10CT020 | Separated Water System | 10CT020 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW |  |  |  |  | 25 | 123 | 250 | - |  |  | TAS3 101-03 | P020NDB10CT020 | CCI-DAT-1466 |  | PRO-PID-0026 |  | mm |  | 2 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020NDB10CT023 | Separated Water System | 10CT023 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT023 | PRO-DAT-0020 |  | PRO-PID-0026 |  | bar(g) |  | 2
P020NDB10CT024 | Separated Water System | 10CT024 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 25 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT024 | PRO-DAT-0020 |  | PRO-PID-0026 |  | bar(g) |  | 2
P020NDB10CT025 | Separated Water System | 10CT025 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 250 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT025 | PRO-DAT-0020 |  | PRO-PID-0026 |  | bar(g) |  | 4
P020NDB10CT026 | Separated Water System | 10CT026 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 20 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT026 | PRO-DAT-0020 |  | PRO-PID-0026 |  | bar(g) |  | 3
P020NDB10CT027 | Separated Water System | 10CT027 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 25 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT027 | PRO-DAT-0020 |  | PRO-PID-0026 |  | mm |  | 25
P020NDB10CT030 | Separated Water System | 10CT030 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW |  |  |  |  | 14 | 120 | 250 | - |  |  | TAS3 101-02 | P020NDB10CT030 | CCI-DAT-1466 |  | PRO-PID-0026 |  | mm |  | 5 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020NDB10CT033 | Separated Water System | 10CT033 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 215 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT033 | PRO-DAT-0020 |  | PRO-PID-0026 |  | uS/cm |  | 2
P020NDB10CT034 | Separated Water System | 10CT034 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 20 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT034 | PRO-DAT-0020 |  | PRO-PID-0026 |  | bar(g) |  | 2
P020NDB10CT035 | Separated Water System | 10CT035 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 25 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT035 | PRO-DAT-0020 |  | PRO-PID-0026 |  | bar(g) |  | 2
P020NDB10CT036 | Separated Water System | 10CT036 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 14 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT036 | PRO-DAT-0020 |  | PRO-PID-0026 |  | bar(g) |  | 60
P020NDB10CT037 | Separated Water System | 10CT037 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 215 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CT037 | PRO-DAT-0020 |  | PRO-PID-0026 |  | bar(g) |  | 60
P020NDB10CY010 | Separated Water System | 10CY010 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY010 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 60
P020NDB10CY011 | Separated Water System | 10CY011 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY011 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 60
P020NDB10CY012 | Separated Water System | 10CY012 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY012 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 3125
P020NDB10CY013 | Separated Water System | 10CY013 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 5640 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY013 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 3125
P020NDB10CY014 | Separated Water System | 10CY014 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 5640 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY014 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 3125
P020NDB10CY020 | Separated Water System | 10CY020 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY020 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 3125
P020NDB10CY021 | Separated Water System | 10CY021 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY021 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 250
P020NDB10CY022 | Separated Water System | 10CY022 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 2680 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY022 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 250
P020NDB10CY023 | Separated Water System | 10CY023 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 14 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY023 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 250
P020NDB10CY024 | Separated Water System | 10CY024 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 75 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY024 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 250
P020NDB10CY030 | Separated Water System | 10CY030 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 14 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY030 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 250
P020NDB10CY031 | Separated Water System | 10CY031 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 75 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY031 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 250
P020NDB10CY032 | Separated Water System | 10CY032 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 14 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY032 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 250
P020NDB10CY033 | Separated Water System | 10CY033 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 75 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY033 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 250
P020NDB10CY034 | Separated Water System | 10CY034 | Pump Station |  | Vendor Supplied Vendor Supplied |  |  |  |  | 14 | Refer to Vendor | See Notes | - |  |  | 0 | P020NDB10CY034 | PRO-DAT-0020 |  | PRO-PID-0026 |  |  |  | 250
P020PCB20CF010 | VSD Cooling Water System | 20CF010 | Pump Station |  | Rosemount 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 75 | 11.78 | TBC | 12 |  |  | TAS3 101-08 | P020PCB20CF010 | CCI-DAT-1474 |  | PRO-PID-0044 |  |  |  | 250
P020PCB20CF020 | VSD Cooling Water System | 20CF020 | Pump Station |  | Rosemount 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ |  |  |  |  | 4500 | 11.78 | TBC | 12 |  |  | TAS3 208-01 | P020PCB20CF020 | CCI-DAT-1474 |  | PRO-PID-0044 |  |  |  | 250
P020PCB20CP010 | VSD Cooling Water System | 20CP010 | Pump Station |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 4500 | 0.9 | -1 to 10.3 | 6 |  |  | TAS3 101-08 | P020PCB20CP010 | CCI-DAT-1461 |  | PRO-PID-0044 |  |  |  | 250
P020PCB20CP040 | VSD Cooling Water System | 20CP040 | Pump Station |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ |  |  |  |  | 5 | 5.82 | -1 to 10.3 | 6 |  |  | TAS3 208-01 | P020PCB20CP040 | CCI-DAT-1461 |  | PRO-PID-0044 |  |  |  | 250
P020PCB20CP510 | VSD Cooling Water System | 20CP510 | Pump Station |  | Wika 72039938+14503369+ |  |  |  |  | 40 | 0.9 | 10 | - |  |  | 0 | P020PCB20CP510 | CCI-DAT-1460 |  | PRO-PID-0044 |  |  |  | 250 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020PCB20CP520 | VSD Cooling Water System | 20CP520 | Pump Station |  | Wika 72039938+14503369+ |  |  |  |  | 5 | 5.82 | 10 | - |  |  | 0 | P020PCB20CP520 | CCI-DAT-1460 |  | PRO-PID-0044 |  |  |  | 250 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020PCB20CP530 | VSD Cooling Water System | 20CP530 | Pump Station |  | Wika 72039938+14503369+ |  |  |  |  | 40 | 5.82 | 10 | - |  |  | 0 | P020PCB20CP530 | CCI-DAT-1460 |  | PRO-PID-0044 |  |  |  | 250 | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10
P020PCB20CT010 | VSD Cooling Water System | 20CT010 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0135SLAR1C2B1UAE065TBXW+114CM0060TAC2SC075AQ35Q5Q8XW |  |  |  |  | 1500 | 30 | 250 | - |  |  | TAS3 101-01 | P020PCB20CT010 | CCI-DAT-1466 |  | PRO-PID-0046 |  |  |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020PCB20CT011 | VSD Cooling Water System | 20CT011 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0135SLAR1C2B1UAE065TBXW+114CM0060TAC2SC075AQ35Q5Q8XW |  |  |  |  | 1500 | 30 | 250 | - |  |  | TAS3 202-01 | P020PCB20CT011 | CCI-DAT-1466 |  | PRO-PID-0046 |  |  |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020PCB20CT012 | VSD Cooling Water System | 20CT012 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0135SLAR1C2B1UAE065TBXW+114CM0060TAC2SC075AQ35Q5Q8XW |  |  |  |  | 16 | 30 | 250 | - |  |  | TAS3 203-01 | P020PCB20CT012 | CCI-DAT-1466 |  | PRO-PID-0046 |  |  |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020PCB22CT011 | VSD Cooling Water System | 22CT011 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW |  |  |  |  | 16 | 40 | 250 | - |  |  | TAS3 101-03 | P020PCB22CT011 | CCI-DAT-1466 |  | PRO-PID-0045 |  |  |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020PCB22CT012 | VSD Cooling Water System | 22CT012 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW |  |  |  |  | 16 | 40 | 250 | - |  |  | TAS3 101-03 | P020PCB22CT012 | CCI-DAT-1466 |  | PRO-PID-0045 |  |  |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020PCB22CT013 | VSD Cooling Water System | 22CT013 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW |  |  |  |  | 16 | 40 | 250 | - |  |  | TAS3 202-01 | P020PCB22CT013 | CCI-DAT-1466 |  | PRO-PID-0045 |  |  |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020PCB22CT021 | VSD Cooling Water System | 22CT021 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | [5 empty] | 30 | 250 | - |  |  | TAS3 101-03 | P020PCB22CT021 | CCI-DAT-1466 |  | PRO-PID-0045 |  |  |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020PCB22CT022 | VSD Cooling Water System | 22CT022 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | [5 empty] | 30 | 250 | - |  |  | TAS3 101-03 | P020PCB22CT022 | CCI-DAT-1466 |  | PRO-PID-0045 |  |  |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020PCB22CT023 | VSD Cooling Water System | 22CT023 | Pump Station |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | [5 empty] | 30 | 250 | - |  |  | TAS3 202-01 | P020PCB22CT023 | CCI-DAT-1466 |  | PRO-PID-0045 |  |  |  | 250 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
P020QFB10CP010 | Instrument Air System | 10CP010 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 10 | -1 to 55 | 12 |  |  | TAS3 101-08 | P020QFB10CP010 | CCI-DAT-1461 |  | PRO-PID-0047 |  |  |  | 250
P020QFB10CP020 | Instrument Air System | 10CP020 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 10 | -1 to 55 | 12 |  |  | TAS3 101-09 | P020QFB10CP020 | CCI-DAT-1461 |  | PRO-PID-0047 |  |  |  | 250
P020QFB10CP030 | Instrument Air System | 10CP030 | Pump Station |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 10 | -1 to 55 | 12 |  |  | TAS3 208-01 | P020QFB10CP030 | CCI-DAT-1461 |  | PRO-PID-0047 |  |  |  | 250
P020QFB10CP040 | Instrument Air System | 10CP040 | Pump Station |  | Rosemount 3051TG3A2B21BB4M4T1Q4Q8S5 c/w 0306RT22BA11 | [5 empty] | 10 | -1 to 55 | 12 |  |  | 0 | P020QFB10CP040 | CCI-DAT-1461 |  | PRO-PID-0047 |  |  |  | 250
P020QFB10CP050 | Instrument Air System | 10CP050 | Pump Station |  | Rosemount 3051TG3A2B21BB4M4T1Q4Q8S5 c/w 0306RT22BA11 | [5 empty] | 10 | -1 to 55 | 12 |  |  | 0 | P020QFB10CP050 | CCI-DAT-1461 |  | PRO-PID-0047 |  |  |  | 250
S020GAC10CL010 | Raw Water System | 10CL010 | Separation Plant |  | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8+751AM1NAB+ | [5 empty] | N/A | See notes | TBC |  |  | TAS2-111-01 | S020GAC10CL010 | CCI-DAT-1468 |  | PRO-PID-0051 |  |  |  | 250
S020GAC10CL011 | Raw Water System | 10CL011 | Separation Plant |  | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8+751AM1NAB+ | [5 empty] | N/A | See notes | TBC |  |  | TAS2-211-01 | S020GAC10CL011 | CCI-DAT-1468 |  | PRO-PID-0051 |  |  |  | 250
S020GAC10CL020 | Raw Water System | 10CL020 | Separation Plant |  | Vendor Supplied Vendor Supplied | [5 empty] | N/A | - | Refer to Notes |  |  | 0 | S020GAC10CL020 | CCI-DAT-1471 PRO-DAT-0088 |  | PRO-PID-0051 |  |  |  | 1200
S020GAC10CL021 | Raw Water System | 10CL021 | Separation Plant |  | Vendor Supplied Vendor Supplied | [5 empty] | N/A | - | Refer to Notes |  |  | 0 | S020GAC10CL021 | CCI-DAT-1471 PRO-DAT-0088 |  | PRO-PID-0051 |  |  |  | 20
S020GAC10CP001 | Raw Water System | 10CP001 | Separation Plant |  | Rosemount 2051CD4A02A1BS5M4Q4 c/w 0305RC52B11B4++ | [5 empty] | 3.49 | 20 | 4 |  |  | TAS2-211-01 | S020GAC10CP001 | CCI-DAT-1462 |  | PRO-PID-0051 |  |  |  | 60 | MVar1: 0; MVar2: 5; MVar3: 10; MVar4: 15; MVar5: 20
S020GAC10CP002 | Raw Water System | 10CP002 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 2.98 | -1 to 10.3 | 5 |  |  | TAS2-211-01 | S020GAC10CP002 | CCI-DAT-1461 |  | PRO-PID-0051 |  |  |  | 60
S020GAC21CP020 | Raw Water System | 21CP020 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 2.98 | -1 to 10.3 | 5 |  |  | TAS2-111-01 | S020GAC21CP020 | CCI-DAT-1461 |  | PRO-PID-0051 |  |  |  | 60
S020GAC22CF501 | Raw Water System | 22CF501 | Separation Plant |  | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | [5 empty] | Refer to Specification | Refer to Specification | - |  |  | 0 | S020GAC22CF501 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  | 2680
S020GAC22CF510 | Raw Water System | 22CF510 | Separation Plant |  | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | [5 empty] | Refer to Specification | Refer to Specification | - |  |  | 0 | S020GAC22CF510 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  | 2680
S020GAC22CF520 | Raw Water System | 22CF520 | Separation Plant |  | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | [5 empty] | Refer to Specification | Refer to Specification | - |  |  | 0 | S020GAC22CF520 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  | 2680
S020GAC22CF530 | Raw Water System | 22CF530 | Separation Plant |  | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | [5 empty] | Refer to Specification | Refer to Specification | - |  |  | 0 | S020GAC22CF530 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  | 5690
S020GAC22CF540 | Raw Water System | 22CF540 | Separation Plant |  | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | [5 empty] | Refer to Specification | Refer to Specification | - |  |  | 0 | S020GAC22CF540 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  | 2680
S020GAC22CF550 | Raw Water System | 22CF550 | Separation Plant |  | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | [5 empty] | Refer to Specification | Refer to Specification | - |  |  | 0 | S020GAC22CF550 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  | 2680
S020GBK10CL010 | Calcite Inhibitor Tank | 10CL010 | Separation Plant |  | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | [5 empty] | N/A | 2500 | 2500 |  |  | 0 | S020GBK10CL010 | CCI-DAT-1468 |  | PRO-PID-0053 |  |  |  | 2680 | MVar1: 0; MVar2: 625; MVar3: 1250; MVar4: 1875; MVar5: 2500
S020GBK10CL011 | Calcite Inhibitor Sump | 10CL011 | Separation Plant |  | Vega PS21.XXXXXGMHB+MBA.BB | [5 empty] | N/A | 1000 | 1000 |  |  | 0 | S020GBK10CL011 | CCI-DAT-1468 |  | PRO-PID-0053 |  |  |  | 250 | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000
S020GBK10CL020 | Calcite Inhibitor Tank | 10CL020 | Separation Plant |  | Vendor Supplied Vendor Supplied | [5 empty] | N/A | 2500 | 2500 |  |  | 0 | S020GBK10CL020 | CCI-DAT-1468 |  | PRO-PID-0053 |  |  |  | 250 | MVar1: 0; MVar2: 625; MVar3: 1250; MVar4: 1875; MVar5: 2500
S020GBK10GS010 | Calcite Inhibitor Tank | 10GS010 | Separation Plant |  | Schneider 56DOL9 Starter + TELE LRD12 Overload | [5 empty] | N/A | - | - |  |  | 0 | S020GBK10GS010 | - |  | PRO-PID-0053 |  |  |  | 250
S020GKA10CL010 | Potable Water System | 10CL010 | Separation Plant |  | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8+751AM1NAB+ | [5 empty] | N/A | See notes | TBC |  |  | TAS2-111-01 | S020GKA10CL010 | CCI-DAT-1468 |  | PRO-PID-0040 |  |  |  | 900
S020GKA10CL011 | Potable Water System | 10CL011 | Separation Plant |  | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8+751AM1NAB+ | [5 empty] | N/A | See notes | TBC |  |  | TAS2-211-01 | S020GKA10CL011 | CCI-DAT-1468 |  | PRO-PID-0040 |  |  |  | 900
S020GKA10CL020 | Potable Water System | 10CL020 | Separation Plant |  | Vendor Supplied Vendor Supplied | [5 empty] | N/A | - | Refer to Notes |  |  | 0 | S020GKA10CL020 | CCI-DAT-1471 PRO-DAT-0074 |  | PRO-PID-0040 |  |  |  | 2680
S020GKA10CL021 | Potable Water System | 10CL021 | Separation Plant |  | Vendor Supplied Vendor Supplied | [5 empty] | N/A | - | Refer to Notes |  |  | 0 | S020GKA10CL021 | CCI-DAT-1471 PRO-DAT-0074 |  | PRO-PID-0040 |  |  |  | 2680
S020GKA20CF191 | Potable Water System | 20CF191 | Separation Plant |  | Wika 72039911++ | [5 empty] | >1.5 | 2 | N/A |  |  | 0 | S020GKA20CF191 | CCI-DAT-1476 |  | PRO-PID-0040 |  |  |  | 2680 | MVar1: 0; MVar2: 0.5; MVar3: 1; MVar4: 1.5; MVar5: 2
S020GKA20CF192 | Potable Water System | 20CF192 | Separation Plant |  | Wika 72039911++ | [5 empty] | >1.5 | 2 | N/A |  |  | 0 | S020GKA20CF192 | CCI-DAT-1476 |  | PRO-PID-0040 |  |  |  | 5440 | MVar1: 0; MVar2: 0.5; MVar3: 1; MVar4: 1.5; MVar5: 2
S020GKA20CF193 | Potable Water System | 20CF193 | Separation Plant |  | Wika 72039911++ | [5 empty] | >1.5 | 2 | N/A |  |  | 0 | S020GKA20CF193 | CCI-DAT-1476 |  | PRO-PID-0040 |  |  |  | 2680 | MVar1: 0; MVar2: 0.5; MVar3: 1; MVar4: 1.5; MVar5: 2
S020GKA20CF194 | Potable Water System | 20CF194 | Separation Plant |  | Wika 72039911++ | [5 empty] | >1.5 | 4 | N/A |  |  | 0 | S020GKA20CF194 | CCI-DAT-1476 |  | PRO-PID-0040 |  |  |  | 2680 | MVar1: 0; MVar2: 1; MVar3: 2; MVar4: 3; MVar5: 4
S020GKA20CF195 | Potable Water System | 20CF195 | Pump Station |  | Wika 72039911++ | [5 empty] | >1.5 | 3 | N/A |  |  | 0 | S020GKA20CF195 | CCI-DAT-1476 |  | PRO-PID-0040 |  |  |  | 2680 | MVar1: 0; MVar2: 0.75; MVar3: 1.5; MVar4: 2.25; MVar5: 3
S020GKA20CP520 | Potable Water System | 20CP520 | Separation Plant |  | Wika 72039882+14503369+ | [5 empty] | 3.14 | 25 | - |  |  | 0 | S020GKA20CP520 | CCI-DAT-1460 |  | PRO-PID-0040 |  |  |  | 25 | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25
S020LCE10CF010 | Process Water System | 10CF010 | Separation Plant |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1195F015A3S1184CBCG2+ | [5 empty] | 3.5 | 5 | 5 |  |  | TAS2-109-01 | S020LCE10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0018 |  |  |  | 250 | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5
S020LCE10CF020 | Process Water System | 10CF020 | Separation Plant |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1195F015A3S1184CBCG2+ | [5 empty] | 1 | 2 | 2 |  |  | TAS2-209-01 | S020LCE10CF020 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0020 |  |  |  | 25 | MVar1: 0; MVar2: 0.5; MVar3: 1; MVar4: 1.5; MVar5: 2
S020LCE10CF030 | Process Water System | 10CF030 | Separation Plant |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1195F015A3S1184CBCG2+ | [5 empty] | 1 | 2 | 2 |  |  | TAS2-109-01 | S020LCE10CF030 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0022 |  |  |  | 250 | MVar1: 0; MVar2: 0.5; MVar3: 1; MVar4: 1.5; MVar5: 2
S020LCE10CF040 | Process Water System | 10CF040 | Separation Plant |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1195F015A3S1184CBCG2+ | [5 empty] | 1 | 2 | 2 |  |  | TAS2-209-01 | S020LCE10CF040 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0024 |  |  |  | 20 | MVar1: 0; MVar2: 0.5; MVar3: 1; MVar4: 1.5; MVar5: 2
S020LCE10CP510 | Process Water System | 10CP510 | Separation Plant |  | Wika 72039876+14503369+0731277 | [5 empty] | 16.72 | 60 | - |  |  | 0 | S020LCE10CP510 | CCI-DAT-1460 |  | PRO-PID-0018 |  |  |  | 25 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
S020LCE10CP520 | Process Water System | 10CP520 | Separation Plant |  | Wika 72039876+14503369+0731277 | [5 empty] | 8.78 | 60 | - |  |  | 0 | S020LCE10CP520 | CCI-DAT-1460 |  | PRO-PID-0020 |  |  |  | 14 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
S020LCE10CP530 | Process Water System | 10CP530 | Separation Plant |  | Wika 72039876+14503369+0731277 | [5 empty] | 1.16 | 60 | - |  |  | 0 | S020LCE10CP530 | CCI-DAT-1460 |  | PRO-PID-0022 |  |  |  | 215 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
S020LCE10CP540 | Process Water System | 10CP540 | Separation Plant |  | Wika 72039876+14503369+0731277 | [5 empty] | 1.16 | 60 | - |  |  | 0 | S020LCE10CP540 | CCI-DAT-1460 |  | PRO-PID-0024 |  |  |  | 20 | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
S020LCE20CL010 | Deoxygenated Tank 1 | 20CL010 | Separation Plant |  | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | [5 empty] | N/A | 3125 | 3125 |  |  | 0 | S020LCE20CL010 | CCI-DAT-1468 |  | PRO-PID-0053 |  |  |  | 25 | MVar1: 0; MVar2: 781.25; MVar3: 1562.5; MVar4: 2343.75; MVar5: 3125
S020LCE20CL011 | Deoxygenated Tank 2 | 20CL011 | Separation Plant |  | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | [5 empty] | N/A | 3125 | 3125 |  |  | 0 | S020LCE20CL011 | CCI-DAT-1468 |  | PRO-PID-0053 |  |  |  | 14 | MVar1: 0; MVar2: 781.25; MVar3: 1562.5; MVar4: 2343.75; MVar5: 3125
S020LCE20CL020 | Deoxygenated Tank 1 | 20CL020 | Separation Plant |  | Vendor Supplied Vendor Supplied | [5 empty] | N/A | 3125 | 3125 |  |  | 0 | S020LCE20CL020 | CCI-DAT-1468 |  | PRO-PID-0053 |  |  |  | 215 | MVar1: 0; MVar2: 781.25; MVar3: 1562.5; MVar4: 2343.75; MVar5: 3125
S020LCE20CL021 | Deoxygenated Tank 2 | 20CL021 | Separation Plant |  | Vendor Supplied Vendor Supplied | [5 empty] | N/A | 3125 | 3125 |  |  | 0 | S020LCE20CL021 | CCI-DAT-1468 |  | PRO-PID-0053 |  |  |  | 2680 | MVar1: 0; MVar2: 781.25; MVar3: 1562.5; MVar4: 2343.75; MVar5: 3125
S020LFC10CT001 | Common Steam/Water Dump System | 10CT001 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 226.1 | 250 | - |  |  | TAS2-201-01 | S020LFC10CT001 | CCI-DAT-1466 |  | PRO-PID-0011 |  |  |  | 2680 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT002 | Common Steam/Water Dump System | 10CT002 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 226.1 | 250 | - |  |  | TAS2-203-01 | S020LFC10CT002 | CCI-DAT-1466 |  | PRO-PID-0011 |  |  |  | 2680 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT003 | Common Steam/Water Dump System | 10CT003 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 226.1 | 250 | - |  |  | TAS2-204-01 | S020LFC10CT003 | CCI-DAT-1466 |  | PRO-PID-0011 |  |  |  | 5640 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT011 | Common Steam/Water Dump System | 10CT011 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 226.1 | 250 | - |  |  | TAS2-101-01 | S020LFC10CT011 | CCI-DAT-1466 |  | PRO-PID-0011 |  |  |  | 5640 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT012 | Common Steam/Water Dump System | 10CT012 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 226.1 | 250 | - |  |  | TAS2-103-01 | S020LFC10CT012 | CCI-DAT-1466 |  | PRO-PID-0011 |  |  |  | 2680 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT013 | Common Steam/Water Dump System | 10CT013 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 226.1 | 250 | - |  |  | TAS2-104-01 | S020LFC10CT013 | CCI-DAT-1466 |  | PRO-PID-0011 |  |  |  | 2680 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT021 | Common Steam/Water Dump System | 10CT021 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 226.1 | 250 | - |  |  | TAS2-101-01 | S020LFC10CT021 | CCI-DAT-1466 |  | PRO-PID-0011 |  |  |  | 2680 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT022 | Common Steam/Water Dump System | 10CT022 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 226.1 | 250 | - |  |  | TAS2-103-01 | S020LFC10CT022 | CCI-DAT-1466 |  | PRO-PID-0011 |  |  |  | 14 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT023 | Common Steam/Water Dump System | 10CT023 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 226.1 | 250 | - |  |  | TAS2-104-01 | S020LFC10CT023 | CCI-DAT-1466 |  | PRO-PID-0011 |  |  |  | 75 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT041 | Common Steam/Water Dump System | 10CT041 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 215 | 250 | - |  |  | TAS2-101-01 | S020LFC10CT041 | CCI-DAT-1466 |  | PRO-PID-0018 |  |  |  | 14 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT042 | Common Steam/Water Dump System | 10CT042 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 215 | 250 | - |  |  | TAS2-102-01 | S020LFC10CT042 | CCI-DAT-1466 |  | PRO-PID-0018 |  |  |  | 75 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT043 | Common Steam/Water Dump System | 10CT043 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 215 | 250 | - |  |  | TAS2-103-01 | S020LFC10CT043 | CCI-DAT-1466 |  | PRO-PID-0018 |  |  |  | 14 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT044 | Common Steam/Water Dump System | 10CT044 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 215 | 250 | - |  |  | TAS2-201-01 | S020LFC10CT044 | CCI-DAT-1466 |  | PRO-PID-0018 |  |  |  | 75 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT045 | Common Steam/Water Dump System | 10CT045 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 215 | 250 | - |  |  | TAS2-202-01 | S020LFC10CT045 | CCI-DAT-1466 |  | PRO-PID-0018 |  |  |  | 14 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT046 | Common Steam/Water Dump System | 10CT046 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 215 | 250 | - |  |  | TAS2-203-01 | S020LFC10CT046 | CCI-DAT-1466 |  | PRO-PID-0018 |  |  |  | 75 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT051 | Common Steam/Water Dump System | 10CT051 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 188 | 250 | - |  |  | TAS2-101-01 | S020LFC10CT051 | CCI-DAT-1466 |  | PRO-PID-0020 |  |  |  | 4500 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT052 | Common Steam/Water Dump System | 10CT052 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 188 | 250 | - |  |  | TAS2-102-01 | S020LFC10CT052 | CCI-DAT-1466 |  | PRO-PID-0020 |  |  |  | 4500 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT053 | Common Steam/Water Dump System | 10CT053 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 188 | 250 | - |  |  | TAS2-103-01 | S020LFC10CT053 | CCI-DAT-1466 |  | PRO-PID-0020 |  |  |  | 5 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT054 | Common Steam/Water Dump System | 10CT054 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 188 | 250 | - |  |  | TAS2-201-01 | S020LFC10CT054 | CCI-DAT-1466 |  | PRO-PID-0020 |  |  |  | 40 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT061 | Common Steam/Water Dump System | 10CT061 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-101-01 | S020LFC10CT061 | CCI-DAT-1466 |  | PRO-PID-0022 |  |  |  | 5 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT062 | Common Steam/Water Dump System | 10CT062 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-102-01 | S020LFC10CT062 | CCI-DAT-1466 |  | PRO-PID-0022 |  |  |  | 40 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT063 | Common Steam/Water Dump System | 10CT063 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-103-01 | S020LFC10CT063 | CCI-DAT-1466 |  | PRO-PID-0022 |  |  |  | 1500 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT064 | Common Steam/Water Dump System | 10CT064 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-201-01 | S020LFC10CT064 | CCI-DAT-1466 |  | PRO-PID-0022 |  |  |  | 1500 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT065 | Common Steam/Water Dump System | 10CT065 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-202-01 | S020LFC10CT065 | CCI-DAT-1466 |  | PRO-PID-0022 |  |  |  | 16 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT066 | Common Steam/Water Dump System | 10CT066 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-203-01 | S020LFC10CT066 | CCI-DAT-1466 |  | PRO-PID-0022 |  |  |  | 16 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT071 | Common Steam/Water Dump System | 10CT071 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-101-01 | S020LFC10CT071 | CCI-DAT-1466 |  | PRO-PID-0024 |  |  |  | 16 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT072 | Common Steam/Water Dump System | 10CT072 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-102-01 | S020LFC10CT072 | CCI-DAT-1466 |  | PRO-PID-0024 |  |  |  | 16 | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT073 | Common Steam/Water Dump System | 10CT073 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-103-01 | S020LFC10CT073 | CCI-DAT-1466 |  | PRO-PID-0024 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT074 | Common Steam/Water Dump System | 10CT074 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-201-01 | S020LFC10CT074 | CCI-DAT-1466 |  | PRO-PID-0024 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT075 | Common Steam/Water Dump System | 10CT075 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-202-01 | S020LFC10CT075 | CCI-DAT-1466 |  | PRO-PID-0024 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020LFC10CT076 | Common Steam/Water Dump System | 10CT076 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | [5 empty] | 143 | 250 | - |  |  | TAS2-203-01 | S020LFC10CT076 | CCI-DAT-1466 |  | PRO-PID-0024 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020NAA10CF010 | Steam System | 10CF010 | Separation Plant |  | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0‐ PGR++ | [5 empty] | 205.5556 | 250 | 250 |  |  | TAS2-209-01 | S020NAA10CF010 | CCI-DAT-1478 |  | PRO-PID-0019 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020NAA10CL410 | Steam System | 10CL410 | Separation Plant |  | Bliss Anand R/36/M/S/2/1/B/N/N/X/PN/S/772MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | - | - | 800 |  |  | 0 | S020NAA10CL410 | CCI-DAT-1471 |  | PRO-PID-0018
S020NAA10CL440 | Steam System | 10CL440 | Separation Plant |  | Bliss Anand R/47/M/S/2/1/B/N/N/X/PN/S/1156MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1200 |  |  | 0 | S020NAA10CL440 | CCI-DAT-1471 |  | PRO-PID-0019
S020NAA10CL450 | Steam System | 10CL450 | Separation Plant |  | Bliss Anand R/47/M/S/2/1/B/N/N/X/PN/S/1156MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1200 |  |  | 0 | S020NAA10CL450 | CCI-DAT-1471 |  | PRO-PID-0019
S020NAA10CL451 | Steam System | 10CL451 | Separation Plant |  | Rosemount 5301HA2P1N4AM00120ABNAM1Q4Q8QTDA1S2+751AM1NAB+ | [5 empty] | N/A | 1200 | 1200 |  |  | TAS2-109-01 | S020NAA10CL451 | CCI-DAT-1469 |  | PRO-PID-0019 |  |  |  |  | MVar1: 0; MVar2: 300; MVar3: 600; MVar4: 900; MVar5: 1200
S020NAA10CL460 | Steam System | 10CL460 | Separation Plant |  | Bliss Anand R/36/M/S/2/1/B/N/N/X/PN/S/772MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 800 |  |  | 0 | S020NAA10CL460 | CCI-DAT-1471 |  | PRO-PID-0019
S020NAA10CP021 | Steam System | 10CP021 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 17 | -1 to 55 | 23 |  |  | TAS2-106-01 | S020NAA10CP021 | CCI-DAT-1461 |  | PRO-PID-0012
S020NAA10CP022 | Steam System | 10CP022 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 17 | -1 to 55 | 23 |  |  | TAS2-107-01 | S020NAA10CP022 | CCI-DAT-1461 |  | PRO-PID-0012
S020NAA10CP023 | Steam System | 10CP023 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 17 | -1 to 55 | 23 |  |  | TAS2-206-01 | S020NAA10CP023 | CCI-DAT-1461 |  | PRO-PID-0012
S020NAA10CP031 | Steam System | 10CP031 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 17 | -1 to 55 | 23 |  |  | TAS4-101-01 | S020NAA10CP031 | CCI-DAT-1461 |  | PRO-PID-0012
S020NAA10CP032 | Steam System | 10CP032 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 17 | -1 to 55 | 23 |  |  | TAS4-102-01 | S020NAA10CP032 | CCI-DAT-1461 |  | PRO-PID-0012
S020NAA10CP033 | Steam System | 10CP033 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 17 | -1 to 55 | 23 |  |  | TAS4-103-01 | S020NAA10CP033 | CCI-DAT-1461 |  | PRO-PID-0012
S020NAA11CF452 | Steam System | 11CF452 | Separation Plant |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P040A3SA065Q8+ | [5 empty] | 10 | 20 | 20 |  |  | TAS2-109-01 | S020NAA11CF452 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0019 |  |  |  |  | MVar1: 0; MVar2: 5; MVar3: 10; MVar4: 15; MVar5: 20
S020NAA20CF010 | Steam System | 20CF010 | Separation Plant |  | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0‐ PGR++ | [5 empty] | 52.7778 | 60 | 60 |  |  | TAS2-209-01 | S020NAA20CF010 | CCI-DAT-1478 |  | PRO-PID-0021 |  |  |  |  | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
S020NAA20CL410 | Steam System | 20CL410 | Separation Plant |  | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 600 |  |  | 0 | S020NAA20CL410 | CCI-DAT-1471 |  | PRO-PID-0020
S020NAA20CL440 | Steam System | 20CL440 | Separation Plant |  | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 600 |  |  | 0 | S020NAA20CL440 | CCI-DAT-1471 |  | PRO-PID-0021
S020NAA20CL450 | Steam System | 20CL450 | Separation Plant |  | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 600 |  |  | 0 | S020NAA20CL450 | CCI-DAT-1471 |  | PRO-PID-0021
S020NAA20CL460 | Steam System | 20CL460 | Separation Plant |  | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 600 |  |  | 0 | S020NAA20CL460 | CCI-DAT-1471 |  | PRO-PID-0021
S020NAA20CL470 | Steam System | 20CL470 | Separation Plant |  | Deleted Deleted | [5 empty] | N/A | - | 600 |  |  | 0 | S020NAA20CL470 | CCI-DAT-1471 |  | PRO-PID-0021
S020NAA20CP021 | Steam System | 20CP021 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 9 | -1 to 55 | 15 |  |  | TAS2-106-01 | S020NAA20CP021 | CCI-DAT-1461 |  | PRO-PID-0013
S020NAA20CP022 | Steam System | 20CP022 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 9 | -1 to 55 | 15 |  |  | TAS2-107-01 | S020NAA20CP022 | CCI-DAT-1461 |  | PRO-PID-0013
S020NAA20CP023 | Steam System | 20CP023 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 9 | -1 to 55 | 15 |  |  | TAS2-207-01 | S020NAA20CP023 | CCI-DAT-1461 |  | PRO-PID-0013
S020NAA20CP031 | Steam System | 20CP031 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 9 | -1 to 55 | 13 |  |  | TAS4-101-01 | S020NAA20CP031 | CCI-DAT-1461 |  | PRO-PID-0013
S020NAA20CP032 | Steam System | 20CP032 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 9 | -1 to 55 | 13 |  |  | TAS4-102-01 | S020NAA20CP032 | CCI-DAT-1461 |  | PRO-PID-0013
S020NAA20CP033 | Steam System | 20CP033 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 9 | -1 to 55 | 13 |  |  | TAS4-103-01 | S020NAA20CP033 | CCI-DAT-1461 |  | PRO-PID-0013
S020NAA31CF010 | Steam System | 31CF010 | Separation Plant |  | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0‐ PGR++ | [5 empty] | 45.2778 | 60 | 60 |  |  | TAS2-109-01 | S020NAA31CF010 | CCI-DAT-1478 |  | PRO-PID-0023 |  |  |  |  | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
S020NAA31CL410 | Steam System | 31CL410 | Separation Plant |  | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA31CL410 | CCI-DAT-1471 |  | PRO-PID-0022
S020NAA31CL440 | Steam System | 31CL440 | Separation Plant |  | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA31CL440 | CCI-DAT-1471 |  | PRO-PID-0023
S020NAA31CL450 | Steam System | 31CL450 | Separation Plant |  | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA31CL450 | CCI-DAT-1471 |  | PRO-PID-0023
S020NAA31CL460 | Steam System | 31CL460 | Separation Plant |  | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA31CL460 | CCI-DAT-1471 |  | PRO-PID-0023
S020NAA31CL470 | Steam System | 31CL470 | Separation Plant |  | Deleted Deleted | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA31CL470 | CCI-DAT-1471 |  | PRO-PID-0023
S020NAA31CP021 | Steam System | 31CP021 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS2-108-01 | S020NAA31CP021 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA31CP022 | Steam System | 31CP022 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS2-109-01 | S020NAA31CP022 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA31CP023 | Steam System | 31CP023 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS2-208-01 | S020NAA31CP023 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA31CP031 | Steam System | 31CP031 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS4-101-01 | S020NAA31CP031 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA31CP032 | Steam System | 31CP032 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS4-102-01 | S020NAA31CP032 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA31CP033 | Steam System | 31CP033 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS4-103-01 | S020NAA31CP033 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA32CF010 | Steam System | 32CF010 | Separation Plant |  | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0‐ PGR++ | [5 empty] | 45 | 60 | 60 |  |  | TAS2-209-01 | S020NAA32CF010 | CCI-DAT-1478 |  | PRO-PID-0025 |  |  |  |  | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60
S020NAA32CL410 | Steam System | 32CL410 | Separation Plant |  | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA32CL410 | CCI-DAT-1471 |  | PRO-PID-0024
S020NAA32CL440 | Steam System | 32CL440 | Separation Plant |  | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA32CL440 | CCI-DAT-1471 |  | PRO-PID-0025
S020NAA32CL450 | Steam System | 32CL450 | Separation Plant |  | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA32CL450 | CCI-DAT-1471 |  | PRO-PID-0025
S020NAA32CL460 | Steam System | 32CL460 | Separation Plant |  | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA32CL460 | CCI-DAT-1471 |  | PRO-PID-0025
S020NAA32CL470 | Steam System | 32CL470 | Separation Plant |  | Deleted Deleted | [5 empty] | N/A | - | 1000 |  |  | 0 | S020NAA32CL470 | CCI-DAT-1471 |  | PRO-PID-0025
S020NAA32CP021 | Steam System | 32CP021 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS2-208-01 | S020NAA32CP021 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA32CP022 | Steam System | 32CP022 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS2-209-01 | S020NAA32CP022 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA32CP023 | Steam System | 32CP023 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS2-108-01 | S020NAA32CP023 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA32CP031 | Steam System | 32CP031 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS4-101-01 | S020NAA32CP031 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA32CP032 | Steam System | 32CP032 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS4-102-01 | S020NAA32CP032 | CCI-DAT-1461 |  | PRO-PID-0014
S020NAA32CP033 | Steam System | 32CP033 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS4-103-01 | S020NAA32CP033 | CCI-DAT-1461 |  | PRO-PID-0014
S020NDA10CL011 | Production Piping System | 10CL011 | Separation Plant |  | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3+751AM1NAB+ | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS4-102-01 | S020NDA10CL011 | CCI-DAT-1469 |  | PRO-PID-0012 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA10CL012 | Production Piping System | 10CL012 | Separation Plant |  | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3+751AM1NAB+ | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | 0 | S020NDA10CL012 | CCI-DAT-1469 |  | PRO-PID-0012 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA10CL013 | Production Piping System | 10CL013 | Separation Plant |  | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3+751AM1NAB+ | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS4-103-01 | S020NDA10CL013 | CCI-DAT-1469 |  | PRO-PID-0012 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA10CL014 | Production Piping System | 10CL014 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | - | 5690 | 5690 |  |  | TAS4-101-01 | S020NDA10CL014 | CCI-DAT-1467 |  | PRO-PID-0012 |  |  |  |  | MVar1: 0; MVar2: 1422.5; MVar3: 2845; MVar4: 4267.5; MVar5: 5690
S020NDA10CL021 | Production Piping System | 10CL021 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS2-106-01 | S020NDA10CL021 | CCI-DAT-1467 |  | PRO-PID-0012 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA10CL022 | Production Piping System | 10CL022 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS2-107-01 | S020NDA10CL022 | CCI-DAT-1467 |  | PRO-PID-0012 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA10CL023 | Production Piping System | 10CL023 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS2-206-01 | S020NDA10CL023 | CCI-DAT-1467 |  | PRO-PID-0012 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA10CL031 | Production Piping System | 10CL031 | Separation Plant |  | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | 1676 | - | 335 to 3018 |  |  | 0 | S020NDA10CL031 | CCI-DAT-1471 |  | PRO-PID-0012
S020NDA10CP010 | Production Piping System | 10CP010 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 17 | -1 to 55 | 23 |  |  | TAS2-106-01 | S020NDA10CP010 | CCI-DAT-1461 |  | PRO-PID-0012
S020NDA10CT010 | Production Piping System | 10CT010 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW | [5 empty] | 217.9 | 250 | 250 |  |  | TAS2-205-01 | S020NDA10CT010 | CCI-DAT-1465 |  | PRO-PID-0011 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020NDA10CT020 | Production Piping System | 10CT020 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0370SLAR1C2B1UAE065TBXW+114CM0295TAC2SC075AQ5Q8R21XW | [5 empty] | 217.9 | 250 | 250 |  |  | TAS2-105-01 | S020NDA10CT020 | CCI-DAT-1465 |  | PRO-PID-0011 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020NDA10CT030 | Production Piping System | 10CT030 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0370SLAR1C2B1UAE065TBXW+114CM0295TAC2SC075AQ5Q8R21XW | [5 empty] | 217.9 | 250 | 250 |  |  | TAS2-105-01 | S020NDA10CT030 | CCI-DAT-1465 |  | PRO-PID-0011 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020NDA20CF010 | Production Piping System | 20CF010 | Separation Plant |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P999A3SD065Q8C0064+ | [5 empty] | 810.28 | 900 | 900 |  |  | TAS2-206-01 | S020NDA20CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0012 |  |  |  |  | MVar1: 0; MVar2: 225; MVar3: 450; MVar4: 675; MVar5: 900
S020NDA20CF020 | Production Piping System | 20CF020 | Separation Plant |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P999A3SD065Q8C0064+ | [5 empty] | 810.28 | 900 | 900 |  |  | TAS2-302-01 | S020NDA20CF020 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0012 |  |  |  |  | MVar1: 0; MVar2: 225; MVar3: 450; MVar4: 675; MVar5: 900
S020NDA20CL011 | Production Piping System | 20CL011 | Separation Plant |  | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS4-101-01 | S020NDA20CL011 | CCI-DAT-1469 |  | PRO-PID-0013 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA20CL012 | Production Piping System | 20CL012 | Separation Plant |  | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS4-102-01 | S020NDA20CL012 | CCI-DAT-1469 |  | PRO-PID-0013 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA20CL013 | Production Piping System | 20CL013 | Separation Plant |  | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS4-103-01 | S020NDA20CL013 | CCI-DAT-1469 |  | PRO-PID-0013 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA20CL014 | Production Piping System | 20CL014 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | - | 5440 | 5440 |  |  | TAS4-102-01 | S020NDA20CL014 | CCI-DAT-1467 |  | PRO-PID-0013 |  |  |  |  | MVar1: 0; MVar2: 1360; MVar3: 2720; MVar4: 4080; MVar5: 5440
S020NDA20CL021 | Production Piping System | 20CL021 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS2-106-01 | S020NDA20CL021 | CCI-DAT-1467 |  | PRO-PID-0013 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA20CL022 | Production Piping System | 20CL022 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS2-107-01 | S020NDA20CL022 | CCI-DAT-1467 |  | PRO-PID-0013 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA20CL023 | Production Piping System | 20CL023 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS2-207-01 | S020NDA20CL023 | CCI-DAT-1467 |  | PRO-PID-0013 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA20CL031 | Production Piping System | 20CL031 | Separation Plant |  | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | 1676 | - | 335 to 3018 |  |  | 0 | S020NDA20CL031 | CCI-DAT-1471 |  | PRO-PID-0013
S020NDA20CP010 | Production Piping System | 20CP010 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 9 | -1 to 55 | 15 |  |  | TAS2-107-01 | S020NDA20CP010 | CCI-DAT-1461 |  | PRO-PID-0013
S020NDA20CR001 | Production Piping System | 20CR001 | Separation Plant |  | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | [5 empty] | * | * | * |  |  | TAS4-104-01 | S020NDA20CR001 | COSASCO Model 3500/3500HT ER-420 |  | PRO-PID-0012
S020NDA20CR002 | Production Piping System | 20CR002 | Separation Plant |  | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | [5 empty] | * | * | * |  |  | TAS4-104-01 | S020NDA20CR002 | COSASCO Model 3500/3500HT ER-420 |  | PRO-PID-0012
S020NDA20CR003 | Production Piping System | 20CR003 | Separation Plant |  | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | [5 empty] | * | * | * |  |  | TAS4-104-01 | S020NDA20CR003 | COSASCO Model 3500/3500HT ER-420 |  | PRO-PID-0012
S020NDA20CR004 | Production Piping System | 20CR004 | Separation Plant |  | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | [5 empty] | * | * | * |  |  | TAS4-104-01 | S020NDA20CR004 | COSASCO Model 3500/3500HT ER-420 |  | PRO-PID-0014
S020NDA21CF010 | Production Piping System | 21CF010 | Separation Plant |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P030A3SA065Q8+ | [5 empty] | 27000 | 0 to 29700 | 0 to 29700 |  |  | TAS2-110-01 | S020NDA21CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0030
S020NDA21CP010 | Production Piping System | 21CP010 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 17 | -1 to 55 | 23 |  |  | TAS2-111-01 | S020NDA21CP010 | CCI-DAT-1461 |  | PRO-PID-0030
S020NDA21CP011 | Production Piping System | 21CP011 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 18.8 | 25 | - |  |  | TAS2-111-01 | S020NDA21CP011 | CCI-DAT-1460 |  | PRO-PID-0030 |  |  |  |  | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25
S020NDA21CT010 | Production Piping System | 21CT010 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | [5 empty] | 202 | 250 | - |  |  | TAS2-111-01 | S020NDA21CT010 | CCI-DAT-1466 |  | PRO-PID-0030 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020NDA22CF020 | Production Piping System | 22CF020 | Separation Plant |  | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P030A3SA065Q8+ | [5 empty] | 27000 | 0 to 29700 | 0 to 29700 |  |  | TAS2-211-01 | S020NDA22CF020 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-0030
S020NDA22CP020 | Production Piping System | 22CP020 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 17 | -1 to 55 | 23 |  |  | TAS2-210-01 | S020NDA22CP020 | CCI-DAT-1461 |  | PRO-PID-0030
S020NDA22CP021 | Production Piping System | 22CP021 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 18.8 | 25 | - |  |  | TAS2-210-01 | S020NDA22CP021 | CCI-DAT-1460 |  | PRO-PID-0030 |  |  |  |  | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25
S020NDA22CT020 | Production Piping System | 22CT020 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | [5 empty] | 202 | 250 | - |  |  | TAS2-211-01 | S020NDA22CT020 | CCI-DAT-1466 |  | PRO-PID-0030 |  |  |  |  | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250
S020NDA23CF011 | Production Piping System | 23CF011 | Separation Plant |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | [5 empty] | Refer to Specification | Refer to Specification | Refer to Specification |  |  | TAS2-107-01 | S020NDA23CF011 | QCM-PRO-SPC-0109 |  | PRO-PID-0101
S020NDA23CP511 | Production Piping System | 23CP511 | Separation Plant |  | Rosemount 3051CD3A02A1BS5M4Q4Q8T1Q15+0305RC52B11B4L4SG | [5 empty] | 0.23 | 20 | Refer to Specification |  |  | TAS2-107-01 | S020NDA23CP511 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  |  | MVar1: 0; MVar2: 5; MVar3: 10; MVar4: 15; MVar5: 20
S020NDA23CP512 | Production Piping System | 23CP512 | Separation Plant |  | Wika 72039878+14503369+0731277 | [5 empty] | 8 | 25 | - |  |  | 0 | S020NDA23CP512 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  |  | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25
S020NDA23CQ010 | Production Piping System | 23CQ010 | Separation Plant |  | E+H CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | [5 empty] | 5 | 14 | 3.5 to 8.5 |  |  | TAS2-110-01 | S020NDA23CQ010 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  |  | MVar1: 0; MVar2: 3.5; MVar3: 7; MVar4: 10.5; MVar5: 14
S020NDA23CT011 | Production Piping System | 23CT011 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | [5 empty] | 60 | 215 | 100 |  |  | TAS2-107-01 | S020NDA23CT011 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  |  | MVar1: 0; MVar2: 53.75; MVar3: 107.5; MVar4: 161.25; MVar5: 215
S020NDA24CF020 | Production Piping System | 24CF020 | Separation Plant |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | [5 empty] | Refer to Specification | Refer to Specification | Refer to Specification |  |  | TAS2-209-01 | S020NDA24CF020 | QCM-PRO-SPC-0109 |  | PRO-PID-0101
S020NDA24CP521 | Production Piping System | 24CP521 | Separation Plant |  | Rosemount 3051CD3A02A1BS5M4Q4Q8T1Q15+0305RC52B11B4L4SG | [5 empty] | 0.23 | 20 | Refer to Specification |  |  | TAS2-207-01 | S020NDA24CP521 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  |  | MVar1: 0; MVar2: 5; MVar3: 10; MVar4: 15; MVar5: 20
S020NDA24CP522 | Production Piping System | 24CP522 | Separation Plant |  | Wika 72039878+14503369+0731277 | [5 empty] | 8 | 25 | - |  |  | 0 | S020NDA24CP522 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  |  | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25
S020NDA24CQ020 | Production Piping System | 24CQ020 | Separation Plant |  | E+H CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | [5 empty] | 5 | 14 | 3.5 to 8.5 |  |  | TAS2-209-01 | S020NDA24CQ020 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  |  | MVar1: 0; MVar2: 3.5; MVar3: 7; MVar4: 10.5; MVar5: 14
S020NDA24CT021 | Production Piping System | 24CT021 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | [5 empty] | 60 | 215 | 100 |  |  | TAS2-207-01 | S020NDA24CT021 | QCM-PRO-SPC-0109 |  | PRO-PID-0101 |  |  |  |  | MVar1: 0; MVar2: 53.75; MVar3: 107.5; MVar4: 161.25; MVar5: 215
S020NDA30CL011 | Production Piping System | 30CL011 | Separation Plant |  | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS4-101-01 | S020NDA30CL011 | CCI-DAT-1469 |  | PRO-PID-0014 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA30CL012 | Production Piping System | 30CL012 | Separation Plant |  | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS4-102-01 | S020NDA30CL012 | CCI-DAT-1469 |  | PRO-PID-0014 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA30CL013 | Production Piping System | 30CL013 | Separation Plant |  | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS4-103-01 | S020NDA30CL013 | CCI-DAT-1469 |  | PRO-PID-0014 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA30CL014 | Production Piping System | 30CL014 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | - | 5640 | 5640 |  |  | TAS4-103-01 | S020NDA30CL014 | CCI-DAT-1467 |  | PRO-PID-0014 |  |  |  |  | MVar1: 0; MVar2: 1410; MVar3: 2820; MVar4: 4230; MVar5: 5640
S020NDA30CL015 | Production Piping System | 30CL015 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | - | 5640 | 5640 |  |  | TAS2-108-01 | S020NDA30CL015 | CCI-DAT-1467 |  | PRO-PID-0014 |  |  |  |  | MVar1: 0; MVar2: 1410; MVar3: 2820; MVar4: 4230; MVar5: 5640
S020NDA30CL021 | Production Piping System | 30CL021 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | 0 | S020NDA30CL021 | CCI-DAT-1467 |  | PRO-PID-0014 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA30CL022 | Production Piping System | 30CL022 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS2-109-01 | S020NDA30CL022 | CCI-DAT-1467 |  | PRO-PID-0014 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA30CL023 | Production Piping System | 30CL023 | Separation Plant |  | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | [5 empty] | 1676 | 2680 | 335 to 3015 |  |  | TAS2-208-01 | S020NDA30CL023 | CCI-DAT-1467 |  | PRO-PID-0014 |  |  |  |  | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680
S020NDA30CL031 | Production Piping System | 30CL031 | Separation Plant |  | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM/20/S/S/P/FLG/X/1/3/NA/21 + 70+80 | [5 empty] | 1676 | - | 335 to 3018 |  |  | 0 | S020NDA30CL031 | CCI-DAT-1471 |  | PRO-PID-0014
S020NDA30CP011 | Production Piping System | 30CP011 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 2.1 | 5 |  |  | TAS2-108-01 | S020NDA30CP011 | CCI-DAT-1461 |  | PRO-PID-0014
S020NDA30CP012 | Production Piping System | 30CP012 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 1 | -1 to 10.3 | 5 |  |  | TAS2-208-01 | S020NDA30CP012 | CCI-DAT-1461 |  | PRO-PID-0014
S020NDB10CP010 | Separated Water System | 10CP010 | Separation Plant |  | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 2.6 | -1 to 10.3 | 10 |  |  | TAS3 101-04 | S020NDB10CP010 | CCI-DAT-1461 |  | PRO-PID-0026
S020NDB11CF011 | Separated Water System | 11CF011 | Separation Plant |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | [5 empty] | Refer to Specification | Refer to Specification | Refer to Specification |  |  | TAS2-111-01 | S020NDB11CF011 | QCM-PRO-SPC-0109 |  | PRO-PID-0100
S020NDB11CQ010 | Separated Water System | 11CQ010 | Separation Plant |  | E+H CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | [5 empty] | 5 | 14 | 3.5 to 8.5 |  |  | TAS2-110-01 | S020NDB11CQ010 | QCM-PRO-DAT-0108 |  | PRO-PID-0100 |  |  |  |  | MVar1: 0; MVar2: 3.5; MVar3: 7; MVar4: 10.5; MVar5: 14
S020NDB11CT011 | Separated Water System | 11CT011 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | [5 empty] | 60 | 75 | 100 |  |  | TAS2-108-01 | S020NDB11CT011 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  |  | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75
S020NDB12CF021 | Separated Water System | 12CF021 | Separation Plant |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | [5 empty] | Refer to Specification | Refer to Specification | Refer to Specification |  |  | TAS2-210-01 | S020NDB12CF021 | QCM-PRO-SPC-0109 |  | PRO-PID-0100
S020NDB12CQ020 | Separated Water System | 12CQ020 | Separation Plant |  | E+H CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | [5 empty] | 5 | 14 | 3.5 to 8.5 |  |  | TAS2-210-01 | S020NDB12CQ020 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  |  | MVar1: 0; MVar2: 3.5; MVar3: 7; MVar4: 10.5; MVar5: 14
S020NDB12CT021 | Separated Water System | 12CT021 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | [5 empty] | 60 | 75 | 100 |  |  | TAS2-208-01 | S020NDB12CT021 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  |  | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75
S020NDB13CF031 | Separated Water System | 13CF031 | Separation Plant |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | [5 empty] | Refer to Specification | Refer to Specification | Refer to Specification |  |  | TAS2-211-01 | S020NDB13CF031 | QCM-PRO-SPC-0109 |  | PRO-PID-0100
S020NDB13CQ030 | Separated Water System | 13CQ030 | Separation Plant |  | E+H CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | [5 empty] | 5 | 14 | 3.5 to 8.5 |  |  | TAS2-211-01 | S020NDB13CQ030 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  |  | MVar1: 0; MVar2: 3.5; MVar3: 7; MVar4: 10.5; MVar5: 14
S020NDB13CT031 | Separated Water System | 13CT031 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | [5 empty] | 60 | 75 | 100 |  |  | TAS2-208-01 | S020NDB13CT031 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  |  | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75
S020NDB14CF041 | Separated Water System | 14CF041 | Separation Plant |  | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | [5 empty] | Refer to Specification | Refer to Specification | Refer to Specification |  |  | TAS2-108-01 | S020NDB14CF041 | QCM-PRO-SPC-0109 |  | PRO-PID-0100
S020NDB14CQ040 | Separated Water System | 14CQ040 | Separation Plant |  | E+H CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | [5 empty] | 5 | 14 | 3.5 to 8.5 |  |  | TAS2-108-01 | S020NDB14CQ040 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  |  | MVar1: 0; MVar2: 3.5; MVar3: 7; MVar4: 10.5; MVar5: 14
S020NDB14CT041 | Separated Water System | 14CT041 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | [5 empty] | 60 | 75 | 100 |  |  | TAS2-108-01 | S020NDB14CT041 | QCM-PRO-SPC-0109 |  | PRO-PID-0100 |  |  |  |  | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75
S020QCM10CL010 | Acid Dosing System | 10CL010 | Separation Plant |  | Vega PS31.XXXXXGMHB +GFLK.ADGX | [5 empty] | N/A | 4500 | TBC |  |  | TAS2-110-01 | S020QCM10CL010 | CCI-DAT-1468 |  | PRO-PID-0029 |  |  |  |  | MVar1: 0; MVar2: 1125; MVar3: 2250; MVar4: 3375; MVar5: 4500
S020QCM10CL020 | Acid Dosing System | 10CL020 | Separation Plant |  | Vega PS31.XXXXXGMHB +GFLK.ADGX | [5 empty] | N/A | 4500 | TBC |  |  | TAS2-210-01 | S020QCM10CL020 | CCI-DAT-1468 |  | PRO-PID-0029 |  |  |  |  | MVar1: 0; MVar2: 1125; MVar3: 2250; MVar4: 3375; MVar5: 4500
S020QCM10CT010 | Acid Dosing System | 10CT010 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | [5 empty] | 20 | -5 to 50 | - |  |  | TAS2-103-01 | S020QCM10CT010 | CCI-DAT-1466 |  | PRO-PID-0029
S020QCM10DL0020 | Acid Dosing System | 10DL0020 | Separation Plant |  | Vega TKALM3-HMI-DB | [5 empty] | N/A | See notes | 0-100% |  |  | 0 | S020QCM10DL0020 | CCI-DAT-1470 |  | PRO-PID-0029
S020QCM10EH011 | Acid Dosing System | 10EH011 | Separation Plant |  | Vega See S020QCM10DL0020 | [5 empty] | N/A | N/A | N/A |  |  | 0 | S020QCM10EH011 | See notes |  | PRO-PID-0029
S020QCM20CF010 | Acid Dosing System | 20CF010 | Separation Plant |  | Rosemount 8705TSA010C3W0G1B3Q4Q8+8732EMT2A2M4+ | [5 empty] | 130 | 0-200 | 0 / 150 |  |  | TAS2-110-01 | S020QCM20CF010 | CCI-DAT-1474 |  | PRO-PID-0030
S020QCM20CP011 | Acid Dosing System | 20CP011 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 18.4 | -1 to 55 | 30 |  |  | TAS2-110-01 | S020QCM20CP011 | CCI-DAT-1461 |  | PRO-PID-0030
S020QCM20CP501 | Acid Dosing System | 20CP501 | Separation Plant |  | Wika 72039899+14503369+ | [5 empty] | 0.3 | 5 | - |  |  | 0 | S020QCM20CP501 | CCI-DAT-1460 |  | PRO-PID-0030 |  |  |  |  | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5
S020QCM20CP510 | Acid Dosing System | 20CP510 | Separation Plant |  | Wika 72039915+14503369+ | [5 empty] | 18.4 | 40 | - |  |  | 0 | S020QCM20CP510 | CCI-DAT-1460 |  | PRO-PID-0030 |  |  |  |  | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40
S020QCM20CT010 | Acid Dosing System | 20CT010 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | [5 empty] | 20 | -5 to 50 | - |  |  | TAS2-101-01 | S020QCM20CT010 | CCI-DAT-1466 |  | PRO-PID-0030
S020QCM21CF020 | Acid Dosing System | 21CF020 | Separation Plant |  | Rosemount 8705TSA010C3W0G1B3Q4Q8+8732EMT2A2M4+ | [5 empty] | 130 | 0-200 | 0 / 150 |  |  | TAS2-210-01 | S020QCM21CF020 | CCI-DAT-1474 |  | PRO-PID-0030
S020QCM21CP021 | Acid Dosing System | 21CP021 | Separation Plant |  | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | [5 empty] | 18.4 | -1 to 55 | 30 |  |  | TAS2-106-01 | S020QCM21CP021 | CCI-DAT-1461 |  | PRO-PID-0030
S020QCM21CP502 | Acid Dosing System | 21CP502 | Separation Plant |  | Wika 72039899+14503369+ | [5 empty] | 0.3 | 5 | - |  |  | TAS2-106-01 | S020QCM21CP502 | CCI-DAT-1460 |  | PRO-PID-0030 |  |  |  |  | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5
S020QCM21CP520 | Acid Dosing System | 21CP520 | Separation Plant |  | Wika 72039915+14503369+ | [5 empty] | 18.4 | 40 | - |  |  | TAS2-106-01 | S020QCM21CP520 | CCI-DAT-1460 |  | PRO-PID-0030 |  |  |  |  | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40
S020QCM21CT020 | Acid Dosing System | 21CT020 | Separation Plant |  | Rosemount 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | [5 empty] | 20 | -5 to 50 | - |  |  | TAS2-106-01 | S020QCM21CT020 | CCI-DAT-1466 |  | PRO-PID-0030
S020QCM30CL031 | Acid Dosing System | 30CL031 | Separation Plant |  | Vega PS21.XXXXXGMHB+MBA.BB | [5 empty] | N/A | 1500 | 1500 |  |  | TAS2-106-01 | S020QCM30CL031 | CCI-DAT-1468 |  | PRO-PID-0029 |  |  |  |  | MVar1: 0; MVar2: 375; MVar3: 750; MVar4: 1125; MVar5: 1500
S020QCM30CL032 | Acid Dosing System | 30CL032 | Separation Plant |  | Vega PS21.XXXXXGMHB+MBA.BB | [5 empty] | N/A | 1500 | 1500 |  |  | TAS2-210-01 | S020QCM30CL032 | CCI-DAT-1468 |  | PRO-PID-0029 |  |  |  |  | MVar1: 0; MVar2: 375; MVar3: 750; MVar4: 1125; MVar5: 1500
S020QCM30CQ010 | Acid Dosing System | 30CQ010 | Separation Plant |  | E+H CLS50D-1009/0 + CYA112-1V02/0 + CM442 CM442-2ER8/0 | [5 empty] | TBC | TBC | TBC |  |  | TAS2-110-01 | S020QCM30CQ010 | See notes |  | PRO-PID-0029
S020SGA10CP401 | Fire Water | 10CP401 | Pump Station |  | Wika 72039878+14503369 | [6 empty] | 16 | - |  |  | 0 | S020SGA10CP401 | CCI-DAT-1460 |  | PRO-PID-0050 |  |  |  |  | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16
S020SGA10CP402 | Fire Water | 10CP402 | Pump Station |  | Wika 72039878+14503369 | [6 empty] | 16 | - |  |  | 0 | S020SGA10CP402 | CCI-DAT-1460 |  | PRO-PID-0050 |  |  |  |  | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16
S020SGA10CP405 | Fire Water | 10CP405 | Pump Station |  | Wika 72039878+14503369 | [6 empty] | 16 | - |  |  | 0 | S020SGA10CP405 | CCI-DAT-1460 |  | PRO-PID-0050 |  |  |  |  | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16
S020SGA10CP406 | Fire Water | 10CP406 | Pump Station |  | Wika 72039878+14503369 | [6 empty] | 16 | - |  |  | 0 | S020SGA10CP406 | CCI-DAT-1460 |  | PRO-PID-0050 |  |  |  |  | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16
Note on B71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Seal Water System until row 342

## Sheet2
Station | System | Tag | Point | Funct | Make | Model | S/No | Criticality | ResCon | PECPR | KPI | NominalValue | Setting | Range | DeviceType | Proof | Loop | PlantCode | Data | StoresNo | DrawingNo | Procs | MVUnit | IdealUnit | MVar1 | MVar2 | MVar3 | MVar4 | MVar5 | MVar6 | MVar7 | IdO1 | IdO2 | IdO3 | IdO4 | IdO5 | IdO6 | IdO7 | Digi1 | Digi2 | Digi3 | Digi4 | Digi5 | Digi6 | DigiAliase1 | DigiAliase2 | DigiAliase3 | DigiAliase4 | DigiAliase5 | DigiAliase6 | DateChecked | CheckedBy
0110LFC10CL010 | Common Steam/Water Dump System | 10CL010 | Wellpad TH11 |  | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | [5 empty] | - | 0 to 6000 | 0 to 6000 |  |  | TH11-7.5.001-01 | 0110LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-0033 |  | mm | mm | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20

## Sheet3
|  | HH | H | L | LL | Digital
PCB20-TI-DT020 | Temperature at Fin Fan Coolers discharge | N/A | TBC | N/A | N/A
1910NDB10-CF010 | TH19N_1 Reinjection Well Flow | N/A | TBC | N/A | N/A
1920NDB10-CF010 | TH19N_2 Reinjection Well Flow | N/A | TBC | N/A | N/A
1930NDB10-CF010 | TH19N_3 Reinjection Well Flow | N/A | TBC | N/A | N/A
1910NDB10-DP010 | TH19N_1 Reinjection Well Pressure | N/A | 45 | N/A | N/A
0190LFC10-CL010 | TH19N Wellpad Pond Level | N/A | TBC | N/A | N/A
1920NDB10-DP010 | TH19N_2 Reinjection Well Pressure | N/A | 45 | N/A | N/A
1930NDB10-DP010 | TH19N_3 Reinjection Well Pressure | N/A | 45 | N/A | N/A
0290NDB10-CP010 | TH29 Reinjection Well Pressure | N/A | 45 | N/A | N/A
0290LFC10-CL010 | TH29 Wellpad Pond Level | N/A | TBC | N/A | N/A
0310NDB10-CP010 | TH31 Reinjection Well Pressure | N/A | 45 | N/A | N/A
EA30NDB10-CP010 | TH35 Reinjection Well Pressure | N/A | 45 | N/A | N/A
0320NDB10-DP010 | TH32 Reinjection Well Pressure | N/A | 45 | N/A | N/A
LCP0LFC10-CL010 | TH32 Wellpad Pond Level | N/A | TBC | N/A | N/A
0330NDB10-DP010 | TH33 Reinjection Well Pressure | N/A | 45 | N/A | N/A
0260NDA10-CF010 | TH26 Production Well Flow | N/A | TBC | TBC | N/A
0260NDA10-CP010 | TH26 Production Well Pressure | N/A | TBC | N/A | N/A
0260LFC10-CL020 | TH26 Wellpad Pond Level | N/A | TBC | N/A | N/A
0300NDA10-CF010 | TH30 Production Well Flow | N/A | TBC | TBC | N/A
0260NDA10-CF010 | TH26 Production Well Pressure | N/A | TBC | TBC | N/A
0300NDA10-CP010 | TH30 Production Well Pressure | N/A | TBC | N/A | N/A
0LFC20-DF011 | TH11 Reinjection Well Flow from GFHP | N/A | TBC | TBC | TBC
0LFC20-CP011 | Pressure transmitter downstream RD | N/A | TBC | N/A | N/A
0110LFC10-CL010 | GFHP Leak Detection - Level | N/A | TBC | N/A | N/A
0120NDA10-CF010 | TH12 Production Well Flow | N/A | TBC | TBC | N/A
0120NDA10-CP010 | TH12 Production Well Pressure | N/A | TBC | N/A | N/A
0120LFC10-CL020 | TH12 Wellpad Pond Level | N/A | TBC | N/A | N/A
0210NDA10-CF010 | TH21 Production Well Flow | N/A | TBC | TBC | N/A
0210NDA10-CP010 | TH21 Production Well Pressure | N/A | TBC | N/A | N/A
0280NDA10-CF010 | TH28 Production Well Flow | N/A | TBC | TBC | N/A
0280NDA10-CP010 | TH28 Production Well Pressure | N/A | TBC | N/A | N/A
0280LFC10-CL020 | TH28 Wellpad Pond Level | N/A | TBC | N/A | N/A
0340NDA10-CF010 | TH34 Production Well Flow | N/A | TBC | TBC | N/A
0340NDA10-CP010 | TH34 Production Well Pressure | N/A | TBC | N/A | N/A
19N0BTL10ET1 | TH19N 110VDC System - Voltage | N/A | N/A | TBC | N/A
19N0BTL10ET2 | TH19N 110VDC System - Current | N/A | N/A | TBC | N/A
19N0CRA10ET1 | PLC Cabinet TH19N - 24Vdc Comms | N/A | N/A | TBC | N/A
19N0CRA10ET2 | PLC Cabinet TH19N - 24Vdc IO | N/A | N/A | TBC | N/A
19N0SAA10CT010 | TH19N Building - Temp | N/A | TBC | TBC | N/A
19N0CRA10VT1A | PLC Cabinet TH19N - 24Vdc VT1A
19N0CRA10VT1B | PLC Cabinet TH19N - 24Vdc VT1B
19N0CRA10VT2A | PLC Cabinet TH19N - 24Vdc VT2A
19N0CRA10VT2B | PLC Cabinet TH19N - 24Vdc VT2B
19N0CRA10HSW1 | PLC Cabinet TH19N - HSW1
19N0CRA10F01 | PLC Cabinet TH19N - Mains Power
19N0CRA10SD1 | PLC Cabinet TH19N - Surge Diverter
19N0CRA10-XG11 | PLC Cabinet TH19N - Security Monitoring
19N0SAA10-XG21 | TH19N BLDG Door - Security Monitoring
19N0BTL10-XG01 | 110VDC System A
19N0BTL10-XG02 | 110VDC System A - Charger Unit
19N0BTL10-XG03 | 110VDC System A - 110VDC Earth
19N0SAA10-XG01 | TH19N Building - H2S Scrubber
19N0SAA10-XG02 | TH19N Building - H2S Scrubber
19N0SAA10-XG03 | TH19N Building - H2S Scrubber
0290BTL10ET1 | TH29 110VDC System - Voltage | N/A | N/A | TBC | N/A
0290BTL10ET2 | TH29 110VDC System - Current | N/A | N/A | TBC | N/A
0290CRA10ET1 | PLC Cabinet TH29 - 24Vdc Comms | N/A | N/A | TBC | N/A
0290CRA10ET2 | PLC Cabinet TH29 - 24Vdc IO | N/A | N/A | TBC | N/A
0290SAA10CT010 | TH29 Building - Temp | N/A | TBC | TBC | N/A
0290CRA10VT1A | PLC Cabinet TH29 - 24Vdc VT1A
0290CRA10VT1B | PLC Cabinet TH29 - 24Vdc VT1B
0290CRA10VT2A | PLC Cabinet TH29 - 24Vdc VT2A
0290CRA10VT2B | PLC Cabinet TH29 - 24Vdc VT2B
0290CRA10HSW1 | PLC Cabinet TH29 - HSW1
0290CRA10F01 | PLC Cabinet TH29 - Mains Power
0290CRA10SD1 | PLC Cabinet TH29 - Surge Diverter
0290CRA10-XG11 | PLC Cabinet TH29 - Security Monitoring
0290SAA10-XG21 | TH29 BLDG Door - Security Monitoring
0290BTL10-XG01 | 110VDC System A -
0290BTL10-XG02 | 110VDC System A - Charger Unit
0290BTL10-XG03 | 110VDC System A - 110VDC Earth
0290SAA10-XG01 | TH29 Building - H2S Scrubber
0290SAA10-XG02 | TH29 Building - H2S Scrubber
0290SAA10-XG03 | TH29 Building - H2S Scrubber
0320BTL10ET1 | TH32 110VDC System - Voltage | N/A | N/A | TBC | N/A
0320BTL10ET2 | TH32 110VDC System - Current | N/A | N/A | TBC | N/A
0320CRA10ET1 | PLC Cabinet TH32 - 24Vdc Comms | N/A | N/A | TBC | N/A
0320CRA10ET2 | PLC Cabinet TH32 - 24Vdc IO | N/A | N/A | TBC | N/A
0320SAA10CT010 | TH32 Building - Temp | N/A | TBC | TBC | N/A
0320CRA10VT1A | PLC Cabinet TH32 - 24Vdc VT1A
0320CRA10VT1B | PLC Cabinet TH32 - 24Vdc VT1B
0320CRA10VT2A | PLC Cabinet TH32 - 24Vdc VT2A
0320CRA10VT2B | PLC Cabinet TH32 - 24Vdc VT2B
0320CRA10HSW1 | PLC Cabinet TH32 - HSW1
0320CRA10F01 | PLC Cabinet TH32 - Mains Power
0320CRA10SD1 | PLC Cabinet TH32 - Surge Diverter
0320CRA10-XG11 | PLC Cabinet TH32 - Security Monitoring
0320SAA10-XG21 | TH32 BLDG Door - Security Monitoring
0320BTL10-XG01 | 110VDC System A -
0320BTL10-XG02 | 110VDC System A - Charger Unit
0320BTL10-XG03 | 110VDC System A - 110VDC Earth
0320SAA10-XG01 | TH32 Building - H2S Scrubber
0320SAA10-XG02 | TH32 Building - H2S Scrubber
0320SAA10-XG03 | TH32 Building - H2S Scrubber
0260BTL10ET1 | TH26 110VDC System - Voltage | N/A | N/A | TBC | N/A
0260BTL10ET2 | TH26 110VDC System - Current | N/A | N/A | TBC | N/A
0260CRA10ET1 | PLC Cabinet TH26 - 24Vdc Comms | N/A | N/A | TBC | N/A
0260CRA10ET2 | PLC Cabinet TH26 - 24Vdc IO | N/A | N/A | TBC | N/A
0260SAA10CT010 | TH26 Building - Temp | N/A | TBC | TBC | N/A
0260CRA10VT1A | PLC Cabinet TH26 - 24Vdc VT1A
0260CRA10VT1B | PLC Cabinet TH26 - 24Vdc VT11B
0260CRA10VT2A | PLC Cabinet TH26 - 24Vdc VT2A
0260CRA10VT2B | PLC Cabinet TH26 - 24Vdc VT2B
0260CRA10HSW1 | PLC Cabinet TH26 - HSW1
0260CRA10F01 | PLC Cabinet TH26 - Mains Power
0260CRA10SD1 | PLC Cabinet TH26 - Surge Diverter
0260CRA10-XG11 | PLC Cabinet TH26 - Security Monitoring
0260SAA10-XG21 | TH26 BLDG Door - Security Monitoring
0260BTL10-XG01 | 110VDC System A -
0260BTL10-XG02 | 110VDC System A - Charger Unit
0260BTL10-XG03 | 110VDC System A - 110VDC Earth
0260SAA10-XG01 | TH26 Building - H2S Scrubber
0260SAA10-XG02 | TH26 Building - H2S Scrubber
0260SAA10-XG03 | TH26 Building - H2S Scrubber
0110BTL10ET1 | TH11 110VDC System - Voltage | N/A | N/A | TBC | N/A
0110BTL10ET2 | TH11 110VDC System - Current | N/A | N/A | TBC | N/A
0110CRA10ET1 | PLC Cabinet TH11 - 24Vdc Comms | N/A | N/A | TBC | N/A
0110CRA10ET2 | PLC Cabinet TH11 - 24Vdc IO | N/A | N/A | TBC | N/A
0110SAA10CT010 | TH11 Building - Temp | N/A | TBC | TBC | N/A
0110CRA10VT1A | PLC Cabinet TH11 - 24Vdc VT1A
0110CRA10VT1B | PLC Cabinet TH11 - 24Vdc VT1B
0110CRA10VT2A | PLC Cabinet TH11 - 24Vdc VTA
0110CRA10VT2B | PLC Cabinet TH11 - 24Vdc VTB
0110CRA10HSW1 | PLC Cabinet TH11 - HSW1
0110CRA10F01 | PLC Cabinet TH11 - Mains Power
0110CRA10SD1 | PLC Cabinet TH11 - Surge Diverter
0110CRA10-XG11 | PLC Cabinet TH11 - Security Monitoring
0110SAA10-XG21 | TH11 BLDG Door - Security Monitoring
0110BTL10-XG01 | 110VDC System A -
0110BTL10-XG02 | 110VDC System A - Charger Unit
0110BTL10-XG03 | 110VDC System A - 110VDC Earth
0110SAA10-XG01 | TH11 Building - H2S Scrubber
0110SAA10-XG02 | TH11 Building - H2S Scrubber
0110SAA10-XG03 | TH11 Building - H2S Scrubber
0120BTL10ET1 | TH12 110VDC System - Voltage | N/A | N/A | TBC | N/A
0120BTL10ET2 | TH12 110VDC System - Current | N/A | N/A | TBC | N/A
0120CRA10ET1 | PLC Cabinet TH12 - 24Vdc Comms | N/A | N/A | TBC | N/A
0120CRA10ET2 | PLC Cabinet TH12 - 24Vdc IO | N/A | N/A | TBC | N/A
0120SAA10CT010 | TH12 Building - Temp | N/A | TBC | TBC | N/A
0120CRA10VT1A | PLC Cabinet TH12 - 24Vdc VT1A
0120CRA10VT1B | PLC Cabinet TH12 - 24Vdc VT1B
0120CRA10VT2A | PLC Cabinet TH12 - 24Vdc VT2A
0120CRA10VT2B | PLC Cabinet TH12 - 24Vdc VT2B
0120CRA10HSW1 | PLC Cabinet TH12 - HSW1
0120CRA10F01 | PLC Cabinet TH12 - Mains Power
0120CRA10SD1 | PLC Cabinet TH12 - Surge Diverter
0120CRA10-XG11 | PLC Cabinet TH12 - Security Monitoring
0120SAA10-XG21 | TH12 BLDG Door - Security Monitoring
0120BTL10-XG01 | 110VDC System A -
0120BTL10-XG02 | 110VDC System A - Charger Unit
0120BTL10-XG03 | 110VDC System A - 110VDC Earth
0120SAA10-XG01 | TH12 Building - H2S Scrubber
0120SAA10-XG02 | TH12 Building - H2S Scrubber
0120SAA10-XG03 | TH12 Building - H2S Scrubber
0280BTL10ET1 | TH28 110VDC System - Voltage | N/A | N/A | TBC | N/A
0280BTL10ET2 | TH28 110VDC System - Current | N/A | N/A | TBC | N/A
0280CRA10ET1 | PLC Cabinet TH28 - 24Vdc Comms | N/A | N/A | TBC | N/A
0280CRA10ET2 | PLC Cabinet TH28 - 24Vdc IO | N/A | N/A | TBC | N/A
0280SAA10CT010 | TH28 Building - Temp | N/A | TBC | TBC | N/A
0280CRA10VT1A | PLC Cabinet TH28 - 24Vdc VT1A
0280CRA10VT1B | PLC Cabinet TH28 - 24Vdc VT1B
0280CRA10VT2A | PLC Cabinet TH28 - 24Vdc VT2A
0280CRA10VT2B | PLC Cabinet TH28 - 24Vdc VT2B
0280CRA10HSW1 | PLC Cabinet TH28 - HSW1
0280CRA10F01 | PLC Cabinet TH28 - Mains Power
0280CRA10SD1 | PLC Cabinet TH28 - Surge Diverter
0280CRA10-XG11 | PLC Cabinet TH28 - Security Monitoring
0280SAA10-XG21 | TH28 BLDG Door - Security Monitoring
0280BTL10-XG01 | 110VDC System A -
0280BTL10-XG02 | 110VDC System A - Charger Unit
0280BTL10-XG03 | 110VDC System A - 110VDC Earth
0280SAA10-XG01 | TH28 Building - H2S Scrubber
0280SAA10-XG02 | TH28 Building - H2S Scrubber
0280SAA10-XG03 | TH28 Building - H2S Scrubber
S020LCE10-CF010 | HP Steam Scrubbing Wash Water FCV Flow | N/A | 13.1 | 1.2 | N/A
S020NAA10-CL451 | Steam Trap Bank HP Steam Scrubbing Level | N/A | 1370 | 190 | N/A
S020LCE10-CF030 | LP Steam Scrubbing A Wash Water FCV Flow | N/A | 2.6 | 0.2 | N/A
S020QCM10-CL010 | Sulphuric Acid Storage Tank Level | N/A | N/A | TBC | N/A
S020QCM10-DL031 | Sulphuric Acid Dosing Sump Pump Level | N/A | TBC | N/A | N/A
S020NAD21-CT010 | Acid Dosing Pump A Suction Pressure | N/A | TBC | N/A | N/A
S020NAD21-CT020 | Acid Dosing Pump B Suction Pressure | N/A | TBC | N/A | N/A
S020NAD21-CP011 | Acid Dosing Pump A Outlet Pressure | N/A | N/A | TBC | N/A
S020NAD22-CP021 | Acid Dosing Pump B Outlet Pressure | N/A | N/A | TBC
S020NAD21-CF010 | Acid Dosing Pump A Outlet Flow | N/A | TBC | TBC | N/A
S020NAD21-CF020 | Acid Dosing Pump B Outlet Flow | N/A | TBC | N/A | N/A
S020GKA10-CL010 | Potable Water Tank 1 Level | N/A | N/A | TBC | N/A
S020GKA10-CP520 | Potable Water Pump Station Out Pressure | N/A | TBC | TBC | N/A
S020GAC10-CL010 | Raw Water Tank 1 Level | N/A | N/A | TBC | N/A
S020GAC21-C020 | Raw Water Pump Station Out Pressure | N/A | TBC | TBC | N/A
S020NDA20-DF021 | HP SGW Drum Outlet Flow | N/A | TBC | TBC | N/A
S020NDA20-GS021 | - |  | TBC
S020LCE10-CF020 | IP Steam Scrubbing Wash Water FCV Flow | N/A | 3 | 0.3 | N/A
S020LCE10-CF040 | LP Steam Scrubbing B Wash Water FCV Flow | N/A | 2.6 | 0.2 | N/A
S020QCM10-DL011 | Sulphuric Acid Storage Tank Level | N/A | TBC | TBC | N/A
S020QCM30-DL031 | Acid Dosing Sump Pump Level | N/A | TBC | N/A | N/A
S020GKA10-CL011 | Potable Water Tank 2 Level | N/A | N/A | TBC | N/A
S020GAC10-CL011 | Raw Water Tank 2 Level | N/A | N/A | TBC | N/A
S020LFC10-CT041 | HP Steam Scrubing Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT051 | IP Steam Scrubing Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT061 | LP Steam Scrubbing A Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT071 | LP Steam Scrubbing B Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT042 | HP Steam Scrubbing Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT062 | LP Steam Scrubbing A Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT052 | IP Steam Scrubbing Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT072 | LP Steam Scrubbing B Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT043 | HP Steam Scrubbing Rupture Disc | N/A | TBC | N/A | N/A
S020LFC10-CT053 | IP Steam Scrubbing Rupture Disc | N/A | TBC | N/A | N/A
S020LFC10-CT063 | LP Steam Scrubbing A Rupture Disc | N/A | TBC | N/A | N/A
S020LFC10-CT073 | LP Steam Scrubbing B Rupture Disc | N/A | TBC | N/A | N/A
S020LFC10-CT021 | TH26 Two Phase Rupture Discs | N/A | TBC | N/A | N/A
S020LFC10-CT022 | TH26 Two Phase Rupture Discs |  | TBC
S020LFC10-CT023 | TH26 Two Phase Rupture Discs | N/A | TBC | N/A | N/A
S020LFC10-CT011 | TH28 Two Phase Rupture Discs Temp | N/A | TBC | N/A | N/A
S020LFC10-CT012 | TH28 Two Phase Rupture Discs Temp |  | TBC
S020LFC10-CT013 | TH28 Two Phase Rupture Discs Temp | N/A | TBC | N/A | N/A
S020LFC10-CT001 | TH12 Two Phase Rupture Discs Temp | N/A | TBC | N/A | N/A
S020LFC10-CT044 | HP Steam Scrubbing Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT054 | IP Steam Scrubbing Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT064 | LP Steam Scrubbing A Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT074 | LP Steam Scrubbing B Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT045 | HP Steam Scrubbing Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT065 | LP Steam Scrubbing A Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT075 | LP Steam Scrubbing B Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT046 | HP Steam Scrubbing Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT066 | LP Steam Scrubbing A Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT076 | LP Steam Scrubbing B Rupture Disc Temp | N/A | TBC | N/A | N/A
S020LFC10-CT002 | TH12 Two Phase Rupture Discs Temp |  | TBC
S020LFC10-CT003 | TH12 Two Phase Rupture Discs Temp | N/A | TBC | N/A | N/A
S020GKA21-CF191 | Acid Dosing Emergency Eye Wash Flow High
S020GKA21-CF192 | Acid Dosing Emergency Eye Wash Flow High
S020GKA21-CF195 | SGW Battery Room Eye Wash Flow High
S020GKA21-CF193 | Acid Dosing Emergency Eye Wash Flow High
S020GKA21-CF194 | SP Battery Room Eye Wash Flow High
S020QHX41-CL010 | HP EDV HPU - Oil Skid Level High
S020QHX41-CP020 | HP EDV HPU - Accumulator Bank Pressure Low
S020QHX42-CL010 | IP EDV HPU - Oil Skid Level High
S020QHX42-CP020 | IP EDV HPU - Accumulator Bank Pressure Low
S020QHX43-CL010 | LP EDV HPU - Oil Skid Level High
S020QHX43-CP020 | LP EDV HPU - Accumulator Bank Pressure Low
S020QHX41-AP001 | HP EDV HPU Pump A - Fault
S020QHX42-AP001 | IP EDV HPU Pump A - Fault
S020QHX43-AP001 | LP EDV HPU Pump A - Fault
S020QHX41-HR001 | HP EDV HPU Heater - Fault
S020QHX42-HR001 | IP EDV HPU Heater - Fault
S020QHX43-HR001 | LP EDV HPU Heater - Fault
S020QHX100-AP001 | HP LCV HPU Pump A - Fault
S020QHX120-AP001 | IP LCV HPU Pump A - Fault
S020QHX150-AP001 | HP/IP/LP HPU Pump A - Fault
S020QHX100-HR001 | HP LCV HPU Heater - Fault
S020QHX120-HR001 | IP LCV HPU Heater - Fault
S020QHX150-HR001 | HP/IP/LP HPU Heater - Fault
S020QCM10-AP010 | Acid Dosing Sump Pump - Fault
S020NDA21-AP010 | Acid Dilution SGW Pump A - Fault
S020QHX100-CL010 | HP LCV HPU - Oil Skid Level High
S020QHX100-CP020 | HP LCV HPU - Accumulator Bank Pressure Low
S020QHX120-CL010 | IP LCV HPU - Oil Skid Level High
S020QHX120-CP020 | IP LCV HPU - Accumulator Bank Pressure Low
S020QHX150-CL010 | HP/IP/LP MDV HPU - Oil Skid Level High High
S020QHX150-CP020 | HP/IP/LP MDV HPU - Acc. Bank Pressure Low
S020QHX41-AP002 | HP EDV HPU Pump B - Fault
S020QHX42-AP002 | IP EDV HPU Pump B - Fault
S020QHX43-AP002 | LP EDV HPU Pump B - Fault
S020QHX100-AP002 | HP LCV HPU Pump B - Fault
S020QHX120-AP002 | IP LCV HPU Pump B - Fault
S020QHX150-AP002 | HP/IP/LP HPU Pump B - Fault
S020NDA21-AP020 | Acid Dilution SGW Pump B - Fault
S020BFA10GS020-Q01 | LV Switchboard Bus A - Incomer Tripped
S020BFT10GT010-CL001 | Local Services Transformer 1 - Oil LevelAlarm
S020BFT10GT010-CT001 | Local Services Transformer 1 - Oil TempAlarm
S020BFT10GT010-CT001 | Local Services Transformer 1 - Winding TempAlarm
S020BFT10GT010-CP001 | Local Services Transformer 1 - Pressure ReliefTrip
S020CRS20-HSW1 | Server Cabinet NSP - HSW1 Fault
S020CRS20-HSW2 | Server Cabinet NSP - HSW2 Fault
S020CRS20-HSW3 | Server Cabinet NSP - HSW3 Fault
S020CRS20-HSW4 | Server Cabinet NSP - HSW4 Fault
S020CRS20-HSW5 | Server Cabinet NSP - HSW5 Fault
S020CRS20-HSW6 | Server Cabinet NSP - HSW6 Fault
S020CRS20-HSW7 | Server Cabinet NSP - HSW7 Fault
S020CRS20-HSW8 | Server Cabinet NSP - HSW9 Fault
S020CRS20-HSW9 | Server Cabinet NSP - HSW10 Fault
S020CRA20-SW1 | PLC Cabinet TAS1 - Security MonitoringAlarm
S020CRA30-SW1 | PLC Cabinet TAS2 - Security MonitoringAlarm
S020CRS20-HSW22 | Server Cabinet NSP - HSW22Fault
S020CRS20-HSW23 | Server Cabinet NSP - HSW23Fault
S020CRS20-HSW24 | Server Cabinet NSP - HSW24Fault
S020CRS20-HSW25 | Server Cabinet NSP - HSW25Fault
S020CRS20-HSW26 | Server Cabinet NSP - HSW26Fault
S020CRS20-HSW27 | Server Cabinet NSP - HSW27Fault
S020CRS20-HSW28 | Server Cabinet NSP - HSW28Fault
S020CRS40-HSW30 | Server Cabinet Building Services - HSW30Fault
S020BTL10-XA2 | 110VDC System A - Charger UnitFault
S020BTL10-XA3 | 110VDC System A - 110VDC EarthFault
S020BRA10-XA1 | 230VAC Inverter A - Inverter UnitFault
S020BFA10GS120-Q01 | LV Switchboard Bus B - IncomerTripped
S020BFT10GT020-CL001 | Local Services Transformer 2 - Oil LevelAlarm
S020BFT10GT020-CT001 | Local Services Transformer 2 - Oil TempAlarm
S020BFT10GT020-CT002 | Local Services Transformer 2 - Winding TempAlarm
S020BFT10GT020-CP001 | Local Services Transformer 2 - Pressure ReliefTrip
S020SGY10-XA1 | Fire System - Alarm
S020SGY10-XA2 | Fire System - Fault
S020SGY10-XA3 | Fire System - VesdaAlarm
S020SGY10-XA4 | Fire System - GasDischarged
S020SAA10-XA1 | HVAC System - Unit 1Fault
S020SAA10-XA2 | HVAC System - Unit 2Fault
S020SAA10-XA3 | HVAC System - Unit 3Fault
S020SAA10-XA4 | HVAC System - Air Purifier 1Fault
S020SAA10-XA5 | HVAC System - Air Purifier 2Fault
S020SAA10-XA6 | HVAC System - Air Purifier 3Fault
TBC | Safety Shower - Unit 1Activated
TBC | Safety Shower - Unit 2Activated
TBC | Safety Shower - Unit 3Activated
S020BTM10-XA2 | 110VDC System B - Charger UnitFault
S020BTM10-XA3 | 110VDC System B - 110VDC EarthFault
S020BRB10-XA1 | 230VAC Inverter B - Inverter UnitFault
S020BFA40K1 | Process DB A - Heat Tracing
S020BFA50K1 | Process DB B - Heat Tracing
P020NDB10-CT010 | SGW Pump A Inlet - Temp | N/A | N/A | TBC | N/A
P020GWA30-CT050 | Seal Water Tanks - Inlet temperature | N/A | TBC | N/A | N/A
P020NDB10-CT030 | SGW Pump C Inlet - Temp | N/A | N/A | TBC | N/A
0110LFC10-CL020 | GFHP Leak Detection - Level | N/A | TBC | N/A | N/A
0110LFC10-CL030 | GFHP Leak Detection - Level | N/A | TBC | N/A | N/A
0110LFC10-CL040 | GFHP Leak Detection - Level | N/A | TBC | N/A | N/A
P020NAB10-CT031 | Condensate Reinjection - Temp | N/A | TBC | N/A | N/A
P020NDB10-CT012 | GFHP Pump A - Temp | TBC | TBC | N/A | N/A
P020NDB10-CT013 | GFHP Pump A - Temp | TBC | TBC | N/A | N/A
P020NDB10-CT014 | GFHP Pump A - Temp | TBC | TBC | N/A | N/A
P020NDB10-CT020 | SGW Pump B Inlet - Temp | N/A | N/A | TBC | N/A
P020GWA31-CT020 | SGW Pump B Seal Water Outlet - Temp | N/A | TBC | N/A | N/A
P020PCB22-CT012 | SGW VSD B Cooling Water - Temp | N/A | TBC | N/A | N/A
P020PCB22-CT011 | SGW VSD A Cooling Water - Temp | N/A | TBC | N/A | N/A
P020NDB10-CP011 | SGW Pump A Inlet - Pressure | N/A | TBC | TBC | TBC
P020NDB10-CP021 | SGW Pump B Inlet - Pressure | N/A | TBC | TBC | TBC
P020GAC20-CL010 | Seal Water Tank 1 - Level | N/A | TBC | TBC | N/A
P020NDB10-CT015 | GFHP Pump A - Temp | N/A | TBC | N/A | N/A
P020NDB10-CT016 | GFHP Pump A - Temp | N/A | TBC | N/A | N/A
P020LFC20-DL004 | Geothermal Fluid Holding Pond - Level | N/A | TBC | TBC | N/A
P020NAB10-DP012 | Condensate Pump A Outlet - Pressure | N/A | TBC | TBC | N/A
P020GWA22-DP010 | Seal Water Pumps Outlet - Pressure | N/A | TBC | TBC | N/A
P020LFC20-CP011 | Condensate pump filter pressure drop | N/A | TBC | N/A | N/A
P020GWA30-CT010 | SGW Pump A Seal Water Outlet - Temp | N/A | TBC | N/A | N/A
P020GWA31-CF020 | SGW Pump B Seal Water Inlet - Flow | N/A | TBC | TBC | TBC
P020GWA31-CF021 | SGW Pump B Seal Water Inlet - Flow | N/A | TBC | TBC | TBC
P020GWA30-CF010 | SGW Pump A Seal Water Inlet - Flow | N/A | TBC | TBC | TBC
P020GWA30-CF011 | SGW Pump A Seal Water Inlet - Flow | N/A | TBC | TBC | TBC
P020PCB20-CL010 | Cooling Water Expansion Vessel - Level | N/A | N/A | TBC | TBC
P020PCB20-CP010 | Coolant Pumps Inlet - Pressure | N/A | TBC | N/A | N/A
P020PCB20-CF010 | Coolant Pump A Outlet - Flow | N/A | N/A | TBC | N/A
P020QFB10-CP010 | Air Receiver A - Pressure | N/A | N/A | TBC | N/A
P020NDB10-CP031 | SGW Pump C Inlet - Pressure | N/A | TBC | TBC | TBC
P020QFB10-CP020 | Air Receiver B - Pressure | N/A | N/A | TBC | N/A
P020LFC20-DT012 | Geothermal Fluid Holding Pond - Temp | N/A | TBC | N/A | N/A
P020GWA32-CT030 | SGW Pump C Seal Water Outlet - Temp | N/A | TBC | N/A | N/A
P020PCB22-CT013 | SGW VSD C Cooling Water - Temp | N/A | TBC | N/A | N/A
P020GWA33-CT040 | SGW Pump D Seal Water Outlet - Temp | N/A | TBC | N/A | N/A
P020NDB10-CT022 | GFHP Pump B - Temp | TBC | TBC | N/A | N/A
P020NDB10-CT023 | GFHP Pump B - Temp | TBC | TBC | N/A | N/A
P020NDB10-CT024 | GFHP Pump B - Temp | TBC | TBC | N/A | N/A
P020GAC20-CL020 | Seal Water Tank 2 - Level | N/A | TBC | TBC | N/A
P020NDB10-CT025 | GFHP Pump B - Temp | N/A | TBC | N/A | N/A
P020NDB10-CT026 | GFHP Pump B - Temp | N/A | TBC | N/A | N/A
P020NAB10-CP031 | Condensate Reinjection - Pressure | N/A | TBC | TBC | N/A
P020GWA21-CP001 | Seal Water Inline Filter Diff - Pressure | N/A | TBC | TBC | N/A
P020GWA32-CF030 | SGW Pump C Seal Water Inlet - Flow | N/A | TBC | TBC | TBC
P020GWA32-CF031 | SGW Pump C Seal Water Inlet - Flow | N/A | TBC | TBC | TBC
P020GWA33-CF040 | SGW Pump D Seal Water Inlet - Flow | N/A | TBC | TBC | TBC
P020GWA33-CF041 | SGW Pump D Seal Water Inlet - Flow | N/A | TBC | TBC | TBC
P020PCB20-CP040 | Coolant Pumps Outlet - Pressure | N/A | TBC | TBC | N/A
P020PCB20-CF020 | Coolant Pump B Outlet - Flow | N/A | N/A | TBC | N/A
P020QFB10-CP030 | Air Receiver C - Pressure | N/A | N/A | TBC | N/A
P020PCB32-AH020_M01 | VSD Cooling Fan Cooler B M01 - Fault
P020PCB32-AH020_M02 | VSD Cooling Fan Cooler B M02 - Fault
P020PCB32-AH020_M03 | VSD Cooling Fan Cooler B M03 - Fault
P020PCB32-AH020_M04 | VSD Cooling Fan Cooler B M04 - Fault
P020GAC30-AH010_M01 | Seal Water Return Fin Fan Cooler - Fault
P020LFC20-AP010 | GFHP Pump B - Fault
P020PCB33-AH030_M01 | VSD Cooling Fan Cooler C M01 - Fault
P020PCB33-AH030_M02 | VSD Cooling Fan Cooler C M02 - Fault
P020PCB33-AH030_M03 | VSD Cooling Fan Cooler C M03 - Fault
P020PCB33-AH030_M04 | VSD Cooling Fan Cooler C M04 - Fault
P020BFA10GS020-Q01 | LV Switchboard Bus A - IncomerTripped
P020BFT10GT010-CL001 | Local Services Transformer 1 - Oil LevelAlarm
P020BFT10GT010-CT001 | Local Services Transformer 1 - Oil TempAlarm
P020BFT10GT010-CT002 | Local Services Transformer 1 - Winding Temp Alarm
P020BFT10GT010-CP001 | Local Services Transformer 1 - Pressure ReliefTrip
P020BFE10GT010-CL001 | SGW Pump A Transformer - Oil LevelAlarm
P020BFE10GT010-CT001 | SGW Pump A Transformer - Oil TempAlarm
P020BFE10GT010-CT002 | SGW Pump A Transformer - Winding TempAlarm
P020BFE10GT010-CP001 | SGW Pump A Transformer - Pressure ReliefTrip
P020CRS10-HSW1 | Server Cabinet NSP - HSW1Fault
P020CRS10-HSW2 | Server Cabinet NSP - HSW2Fault
P020CRS10-HSW3 | Server Cabinet NSP - HSW3Fault
P020CRS10-HSW4 | Server Cabinet NSP - HSW4Fault
P020CRS10-HSW5 | Server Cabinet NSP - HSW5Fault
P020CRS10-HSW6 | Server Cabinet NSP - HSW6Fault
P020CRS10-HSW7 | Server Cabinet NSP - HSW7Fault
P020CRS10-HSW8 | Server Cabinet NSP - HSW8Fault
P020CRS10-HSW9 | Server Cabinet NSP - HSW9Fault
P020CRS10-HSW10 | Server Cabinet NSP - HSW10Fault
P020CRS30-HSW30 | Server Cabinet Building Services - HSW30Fault
P020CRA10-SW1 | PLC Cabinet TAS3 - Security MonitoringAlarm
P020BBA10GS030-Q01 | 11kV Switchboard Bus A - Unison IncomerTripped
P020BBA10GS020-Q01 | 11kV Switchboard Bus A - IncomerTripped
P020BBA10GS010-Q01 | 11kV Switchboard Bus A - BustieTripped
P020BBA10GS040-Q01 | 11kV Switchboard Bus A - LST1 FeederTripped
P020BBA10GS050-Q01 | 11kV Switchboard Bus A - SGW Pump A FeederTripped
P020BTL10-XA2 | 110VDC System A - Charger UnitFault
P020BTL10-XA3 | 110VDC System A - 110VDC EarthFault
P020BRA10-XA1 | 230VAC Inverter A - Inverter UnitFault
P020BFA10GS120-Q01 | LV Switchboard Bus B - IncomerTripped
P020BFT10GT020-CL001 | Local Services Transformer 2 - Oil LevelAlarm
P020BFT10GT020-CT001 | Local Services Transformer 2 - Oil TempAlarm
P020BFT10GT020-CT002 | Local Services Transformer 2 - Winding TempAlarm
P020BFT10GT020-CP001 | Local Services Transformer 2 - Pressure ReliefTrip
P020BFE10GT020-CL001 | SGW Pump B Transformer - Oil LevelAlarm
P020BFE10GT020-CT001 | SGW Pump B Transformer - Oil TempAlarm
P020BFE10GT020-CT002 | SGW Pump B Transformer - Winding TempAlarm
P020BFE10GT020-CP001 | SGW Pump B Transformer - Pressure ReliefTrip
P020SGY10-XA1 | Fire System - Alarm
P020SGY10-XA2 | Fire System - Fault
P020SGY10-XA3 | Fire System - VesdaAlarm
P020SGY10-XA4 | Fire System - GasDischarged
P020SAA10-XA1 | HVAC System - Unit 1Fault
P020SAA10-XA2 | HVAC System - Unit 2Fault
P020SAA10-XA3 | HVAC System - Unit 3Fault
P020SAA10-XA4 | HVAC System - Air Purifier 1Fault
P020SAA10-XA5 | HVAC System - Air Purifier 2Fault
P020SAA10-XA6 | HVAC System - Air Purifier 3Fault
TBC | Safety Shower - Unit 1Activated
TBC | Safety Shower - Unit 2Activated
TBC | Safety Shower - Unit 3Activated
P020BBA10GS120-Q01 | 11kV Switchboard Bus B - IncomerTripped
P020BBA10GS110-Q01 | 11kV Switchboard Bus B - BustieTripped
P020BBA10GS140-Q01 | 11kV Switchboard Bus B - LST2 FeederTripped
P020BBA10GS130-Q01 | 11kV Switchboard Bus B - SP Tx FeederTripped
P020BBA10GS150-Q01 | 11kV Switchboard Bus B - SGW Pump B FeederTripped
P020BBA10GS160-Q01 | 11kV Switchboard Bus B - SGW Pump C FeederTripped
P020BTM10-XA2 | 110VDC System B - Charger UnitFault
P020BTM10-XA3 | 110VDC System B - 110VDC EarthFault
P020BRB10-XA1 | 230VAC Inverter B - Inverter UnitFault
P020BFE10GT030 | SGW Pump C Transformer - Oil LevelAlarm
P020BFE10GT030 | SGW Pump C Transformer - Oil TempAlarm
P020BFE10GT030 | SGW Pump C Transformer - Winding TempAlarm
P020BFE10GT030 | SGW Pump C Transformer - Pressure ReliefTrip
P020LDAH024 | HP SGW Drum Level Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
P020LI20-DL024 | HP SGW Drum Level Transmitter | N/A | TBC | TBC | N/A
P020PDAH021 | HP SGW Drum Pressure Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
P020PI20-DP901 | HP SGW Drum Pressure Transmitter | N/A | TBC | TBC | N/A
P020LDAH014 | HP SGW Drum Level SIS Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
P020LI20-DL014 | HP SGW Drum SIS Level Transmitter | N/A | TBC | TBC | N/A
P020LDAH024 | IP SGW Drum Level Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
P020LI20-DL024 | IP SGW Drum Level Transmitter | N/A | TBC | TBC | N/A
P020PDAH021 | IP SGW Drum Pressure Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
P020PI20-DP901 | IP SGW Drum Pressure Transmitter | N/A | TBC | TBC | N/A
P020LDAH014 | IP SGW Drum Level SIS Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
P020LI20-DL014 | IP SGW Drum SIS Level Transmitter | N/A | TBC | TBC | N/A
P020LDAH024 | LP SGW Drum Level Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
P020LI20-DL024 | LP SGW Drum Level Transmitter | N/A | TBC | TBC | N/A
P020PDAH901A | LP SGW Drum Pressure Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
P020PDAH901B | LP SGW Drum Pressure Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
P020PI20-DP901 | LP SGW Drum Pressure Transmitter | N/A | TBC | TBC | N/A
P020LI20-CL014 | LP SGW Drum SIS Level Transmitter | N/A | TBC | N/A | N/A
P020LI20-CL015 | LP SGW Drum SIS Level Transmitter | N/A | TBC | N/A | N/A
L050NDA10-CP010 | TH12 Two Phase production line pressure | N/A | TBC | N/A | N/A
L060NDA10-CP010 | TH28 Two Phase production line pressure | N/A | TBC | N/A | N/A
L070NDA10-CP010 | TH26 Two Phase production line pressure | N/A | TBC | N/A | N/A
P020LI20-CL014 | HP SGW Drum SIS Level Transmitter | N/A | TBC | N/A | N/A
S020NDA20-CR005 | - | N/A | TBC | N/A | N/A
P020LI20-CL014 | HP SGW Drum SIS Level Transmitter | N/A | TBC | N/A | N/A
P020NDB10-CT013 | SGW Pump A temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT014 | SGW Pump A temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT015 | SGW Pump A temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT016 | SGW Pump A temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT017 | SGW Pump A temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT023 | SGW Pump B temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT024 | SGW Pump B temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT025 | SGW Pump B temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT026 | SGW Pump B temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT027 | SGW Pump B temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT033 | SGW Pump C temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT034 | SGW Pump C temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT035 | SGW Pump C temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT036 | SGW Pump C temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-CT037 | SGW Pump C temperature transmitter | TBC | TBC | N/A | N/A
P020NDB10-DY010 | SGW Pump A vibration sensor transmitter transmitter | N/A | TBC | N/A | N/A
P020NDB10-DY020 | SGW Pump B vibration sensor transmitter transmitter | N/A | TBC | N/A | N/A
P020NDB10-DY030 | SGW Pump C vibration sensor transmitter transmitter | N/A | TBC | N/A | N/A
P020NAB10-CT012 | Condenate Pump - Temp | TBC | TBC | N/A | N/A
P020NAB10-CT013 | Condenate Pump - Temp | TBC | TBC | N/A | N/A
P020NAB10-CT014 | Condenate Pump - Temp | TBC | TBC | N/A | N/A
P020NAB10-CT015 | Condenate Pump - Temp | TBC | TBC | N/A | N/A
P020NAB10-CT016 | Condenate Pump - Temp | TBC | TBC | N/A | N/A
S020QCM10-DL020 | Sulphuric Acid Storage Tank Level | N/A | TBC | N/A | N/A
S020QCM30-CQ010 | Acid Dosing Sump Pump pH level | N/A | TBC | N/A | N/A
S020QCM20-CF010 | Acid Dosing Pump A Magnetic Flow | N/A | TBC | TBC | N/A
S020QCM21-CF020 | Acid Dosing Pump B Magnetic Flow | N/A | TBC | TBC | N/A
S020QCM20-CP011 | Acid Dosing Pump A Pressure discharge | N/A | TBC | N/A | N/A
S020QCM21-CP021 | Acid Dosing Pump B Pressure discharge | N/A | TBC | N/A | N/A
0NAB10-CF010 | TH11 Reinjection Well Flow | N/A | TBC | TBC | N/A
0NAB10FDAH011 | TH11 Reinjection Well Flow | N/A | TBC | N/A | N/A
0NAB10-DP010 | TH11 Reinjection Well Flow | N/A | TBC | N/A | N/A
0LFC10-CL010 | TH11 wellpad pond level | N/A | TBC | N/A | N/A
L070LFC10-CL010 | ORH pond level | N/A | TBC | N/A | N/A
S020LDAH011 | Sulphuric Acid Storage Tank Level | N/A | TBC | N/A | N/A
S020LAH011 | Sulphuric Acid Storage Tank Level | N/A | TBC | N/A | N/A
P030LDAH031 | Acid Dosing Sump Pump Level | N/A | TBC | N/A | N/A
P020FDAH012 | Acid Dosing Pumps Flow | N/A | TBC | N/A | N/A
P020FDAH011 | Acid Dosing Pump A discharge pressure | N/A | TBC | N/A | N/A
P020FDAH021 | Acid Dosing Pump B discharge pressure | N/A | TBC | N/A | N/A
P020GAC20-CL011 | Seal Water Tanks sump pump bound Level | N/A | TBC | N/A | N/A
P020LI20-DL014 | LP SGW Drum SIS Level Transmitter Deviation Alarm | N/A | TBC | N/A | N/A
LCP2-2-CF010 | LCP2-2 Reinjection Well Flow | N/A | TBC | N/A | N/A
LCP2-1-CF010 | LCP2-1 Reinjection Well Flow | N/A | TBC | N/A | N/A
S020LCE20-CL011 | Deoxygenated Process Water Tank 2 Level | N/A | N/A | TBC | N/A
S020LCE20-CL010 | Deoxygenated Process Water Tank 1 Level | N/A | N/A | TBC | N/A
S020GBK10-CL010 | Calcite Inhibitor Tank Level | N/A | N/A | TBC | N/A
S020GBK10-CL011 | Calcite Inhibitor Dosing Sump | N/A | N/A | TBC | N/A
S020NDB11-CT011 | LP pH Monitoring Temp | N/A | TBC | N/A | N/A
S020NDB12-CT021 | LP pH Monitoring Temp | N/A | TBC | N/A | N/A
S020NDB13-CT031 | LP pH Monitoring Temp | N/A | TBC | N/A | N/A
S020NDB14-CT041 | LP pH Monitoring Temp | N/A | TBC | N/A | N/A
S020NDB11-CF011 | LP pH Monitoring Flow | N/A | TBC | TBC | N/A
S020NDB12-CF021 | LP pH Monitoring Flow | N/A | TBC | TBC | N/A
S020NDB13-CF031 | LP pH Monitoring Flow | N/A | TBC | TBC | N/A
S020NDB14-CF041 | LP pH Monitoring Flow | N/A | TBC | TBC | N/A
S020NDA23-CT011 | HP pH Monitoring Temp | N/A | TBC | N/A | N/A
S020NDA24-CT021 | HP pH Monitoring Temp | N/A | TBC | N/A | N/A
S020NDA23-CF011 | HP pH Monitoring Flow | N/A | TBC | TBC | N/A
S020NDA24-CF021 | HP pH Monitoring Flow | N/A | TBC | TBC | N/A
S020NDA23-CP511 | HP pH Monitoring Pressure Difference | N/A | TBC | N/A | N/A
S020NDA24-CP521 | HP pH Monitoring Pressure Difference | N/A | TBC | N/A | N/A
P020CI20-CI005 | Corrosometer Transmitters Common Alarm | N/A | TBC | N/A | N/A
P020LI20-DL024 | HP SGW Loop Seal Level | N/A | TBC | N/A | N/A
P020LI20-DL024 | IP SGW Loop Seal Level | N/A | TBC | N/A | N/A
P020LI20-DL024 | LP SGW Loop Seal A Level | N/A | TBC | N/A | N/A
P020LI20-DL024 | LP SGW Loop Seal B Level | N/A | TBC | N/A | N/A

## Sheet4
P020NDB10AA110 | Motor operated valve | SGW PUMP A OUTLET MOV | ROTORK | IQ90 | Elecric actuator
P020NDB10AA120 | Motor operated valve | SGW PUMP B OUTLET MOV | ROTORK | IQ90 | Elecric actuator
P020NDB10AA130 | Motor operated valve | SGW PUMP C OUTLET MOV | ROTORK | IQ90 | Elecric actuator
P020NDB10AA140 | Motor operated valve | SGW PUMPS BYPASS MOV | ROTORK | TBA | Elecric actuator
L190NDB10AA001 | Motor operated valve | SGW CROSS COUNTRY LINE A MOV | ROTORK | TBA | Elecric actuator
L190NDB10AA002 | Motor operated valve | SGW CROSS COUNTRY LINE A MOV | ROTORK | IQ35 | Elecric actuator
L200NDB10AA001 | Motor operated valve | SGW CROSS COUNTRY LINE B MOV | ROTORK | IQ35 | Elecric actuator
L200NDB10AA002 | Motor operated valve | SGW CROSS COUNTRY LINE B MOV | ROTORK | IQ35 | Elecric actuator
P020NAB10AA030 | Motor operated valve | CONDENSATE PUMP A OUTLET MOV | ROTORK | TBA | Elecric actuator
P020NAB10AA110 | Motor operated valve | CONDENSATE PUMPS BYPASS MOV | ROTORK | IQ18 | Elecric actuator
P020LFC20AA010 | Motor operated valve | GFHP PUMP A OUTLET MOV | ROTORK | IQ18 | Elecric actuator
P020LFC20AA020 | Motor operated valve | GFHP PUMP B OUTLET MOV | ROTORK | IQ18 | Elecric actuator
S020NDB10AA053 | Motor operated valve | LP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB10AA054 | Motor operated valve | LP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB10AA013 | Motor operated valve | LP EDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB10AA023 | Motor operated valve | LP EDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB10AA033 | Motor operated valve | LP EDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA10AA043 | Motor operated valve | LP EDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA020 | Motor operated valve | LP SEPARATOR B OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDB30AA021 | Motor operated valve | LP SEPARATOR B OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S060NDB10AA001 | Motor operated valve | LP SEPARATOR OUTLET MOV | ROTORK | IQ35 | Elecric actuator
L060NDA10AA030 | Motor operated valve | TH28 TO HP SEPARATOR MOV | ROTORK | IQ35 | Elecric actuator
L060NDA10AA040 | Motor operated valve | TH28 TO SILENCER MOV | ROTORK | IQ35 | Elecric actuator
L060NDA10AA050 | Motor operated valve | TH12 TO SILENCER MOV | ROTORK |  | Elecric actuator
L070NDA10AA030 | Motor operated valve | TH26 TO HP SEPARATOR MOV | ROTORK | IQ35 | Elecric actuator
L070NDA10AA040 | Motor operated valve | TH26 TO SILENCER MOV | ROTORK | IQ35 | Elecric actuator
L050NDA10AA030 | Motor operated valve | TH12 TO HP SEPARATOR MOV | ROTORK | IQ35 | Elecric actuator
L050NDA10AA040 | Motor operated valve | TH12 TO SILENCER MOV | ROTORK | IQ35 | Elecric actuator
S020NAA11AA110 | Motor operated valve | HP CDPS MOV | ROTORK | TBA | Elecric actuator
S020NAA10AA140 | Motor operated valve | HP SCRUBBER MOV | ROTORK | TBA | Elecric actuator
S020NAA31AA055 | Motor operated valve | LP STEAM SCRUBBING LINE A MOV | ROTORK | IQ40 | Elecric actuator
S020NAA31AA056 | Motor operated valve | LP STEAM SCRUBBING LINE A MOV | ROTORK | IQ40 | Elecric actuator
S020NAA32AA055 | Motor operated valve | LP STEAM SCRUBBING LINE B MOV | ROTORK | IQ40 | Elecric actuator
S020NAA32AA056 | Motor operated valve | LP STEAM SCRUBBING LINE B MOV | ROTORK | IQ40 | Elecric actuator
S020NAA10AA001 | Motor operated valve | HP STEAM SCRUBBING LINE MOV | ROTORK | IQ90 | Elecric actuator
S020NAA10AA002 | Motor operated valve | HP STEAM SCRUBBING LINE MOV | ROTORK | IQ90 | Elecric actuator
S020NAA20AA001 | Motor operated valve | IP STEAM SCRUBBING LINE MOV | ROTORK | IQ35 | Elecric actuator
S020NAA20AA002 | Motor operated valve | IP STEAM SCRUBBING LINE MOV | ROTORK | IQ35 | Elecric actuator
S020NAA31AA001 | Motor operated valve | LP STEAM SCRUBBING LINE A MOV | ROTORK | IQ90 | Elecric actuator
S020NAA31AA002 | Motor operated valve | LP STEAM SCRUBBING LINE A MOV | ROTORK | IQ90 | Elecric actuator
S020NAA32AA001 | Motor operated valve | LP STEAM SCRUBBING LINE B MOV | ROTORK | IQ90 | Elecric actuator
S020NAA32AA002 | Motor operated valve | LP STEAM SCRUBBING LINE B MOV | ROTORK | IQ90 | Elecric actuator
S020NDA20AA013 | Motor operated valve | HP LCV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA023 | Motor operated valve | HP LCV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA033 | Motor operated valve | HP LCV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA041 | Motor operated valve | HP EDV INLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA051 | Motor operated valve | HP EDV INLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA061 | Motor operated valve | HP EDV INLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA071 | Motor operated valve | HP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA072 | Motor operated valve | HP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA20AA001 | Motor operated valve | HP SEPARATOR OUTLET MOV | ROTORK | IQ70 | Elecric actuator
S020NDA20AA002 | Motor operated valve | HP SEPARATOR OUTLET MOV | ROTORK | IQ70 | Elecric actuator
S020NDA20AA043 | Motor operated valve | HP EDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA20AA053 | Motor operated valve | HP EDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA20AA063 | Motor operated valve | HP EDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA20AA073 | Motor operated valve | HP MDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA20AA074 | Motor operated valve | HP MDV OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NDA30AA010 | Motor operated valve | LP SEPARATOR A OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA011 | Motor operated valve | LP SEPARATOR A OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA013 | Motor operated valve | IP LCV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA023 | Motor operated valve | IP LCV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA033 | Motor operated valve | IP LCV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA043 | Motor operated valve | IP LCV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA053 | Motor operated valve | IP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA054 | Motor operated valve | IP MDV OUTLET MOV | ROTORK | IQ35 | Elecric actuator
S020NDA30AA063 | Motor operated valve | IP EDV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA073 | Motor operated valve | IP EDV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA083 | Motor operated valve | IP EDV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA093 | Motor operated valve | IP EDV OUTLET MOV | ROTORK | IQ25 | Elecric actuator
S020NDA30AA001 | Motor operated valve | IP SEPARATOR OUTLET MOV | ROTORK | IQ40 | Elecric actuator
S020NAA31AA006 | Motor operated valve | LP SCRUBBING LINE BYPASS MOV | ROTORK | IQ40 | Elecric actuator
S020NAA31AA007 | Motor operated valve | LP SCRUBBING LINE BYPASS MOV | ROTORK | IQ40 | Elecric actuator
S020NDB10AA043 | Motor operated valve | LP EDV Outlet MOV | ROTORK |  | Elecric actuator
S020NDB10AA001 | Motor operated valve | LP Separator Outlet MOV | ROTORK |  | Elecric actuator
S020NDA30AA021 | Motor operated valve | LP Separator B Outlet MOV | ROTORK |  | Elecric actuator
S020GAC10AA021 | Motor operated valve | RAW WATER SYSTEM MOV | ROTORK |  | Elecric actuator
S020GAC10AA031 | Motor operated valve | RAW WATER SUPPLY MOV | ROTORK |  | Elecric actuator

## Sheet5
TAG | FULL KKS | TYPE | DESCRIPTION | PID
P020BFE10GU010_-M01 | TH00P020BFE10GU010_-M01 | Motor | SGW PUMP A VSD COOLANT PUMP MOTOR
P020BFE10GU020_-M01 | TH00P020BFE10GU020_-M01 | Motor | SGW PUMP B VSD COOLANT PUMP MOTOR
P020BFE10GU030_-M01 | TH00P020BFE10GU030_-M01 | Motor | SGW PUMP C VSD COOLANT PUMP MOTOR
P020GWA20AP020_-M01 | TH00P020GWA20AP020_-M01 | Motor | Seal water bund sump pump motor
P020GWB10AP010_-M01 | TH00P020GWB10AP010_-M01 | Motor | GFHP Seal Water Pump A Motor
P020GWB10AP020_-M01 | TH00P020GWB10AP020_-M01 | Motor | GFHP Seal Water Pump B Motor
P020GWA22AP010_-M01 | TH00P020GWA22AP010_-M01 | Motor | Seal Water Supply Pump A Motor
P020GWA22AP020_-M01 | TH00P020GWA22AP020_-M01 | Motor | Seal Water Supply Pump B Motor
P020GWA22AP030_-M01 | TH00P020GWA22AP030_-M01 | Motor | Seal Water Supply Pump C Motor
P020GWA30AH010_-M01 | TH00P020GWA30AH010_-M01 | Motor | Seal Water Return Fin Fan Cooler Motor 1
P020GWA30AH010_M02 | TH00P020GWA30AH010_M02 | Motor | Seal Water Return Fin Fan Cooler Motor 2
P020LFC20AP010_-M01 | TH00P020LFC20AP010_-M01 | Motor | GEOTHERMAL FLUID HOLDING POND (GFHP) PUMP A Motor
P020LFC20AP020_-M01 | TH00P020LFC20AP020_-M01 | Motor | GEOTHERMAL FLUID HOLDING POND (GFHP) PUMP B Motor
P020NAB10AP010_-M01 | TH00P020NAB10AP010_-M01 | Motor | Condensate Pump A Motor
P020NAB10AP020_-M01 | TH00P020NAB10AP020_-M01 | Motor | Condensate pump B Motor
P020NDB10AP010_-M01 | TH00P020NDB10AP010_-M01 | Motor | SGW REINJECTION PUMP A MOTOR (50%)
P020NDB10AP020_-M01 | TH00P020NDB10AP020_-M01 | Motor | SGW REINJECTION PUMP B MOTOR (50%)
P020NDB10AP030_-M01 | TH00P020NDB10AP030_-M01 | Motor | SGW REINJECTION PUMP C MOTOR (50%)
P020PCB20AP010_-M01 | TH00P020PCB20AP010_-M01 | Motor | SGW Pump VSD Cooling Circ Pump A Motor
P020PCB20AP020_-M01 | TH00P020PCB20AP020_-M01 | Motor | SGW Pump VSD Cooling Circ Pump B Motor
P020PCB20AP030_-M01 | TH00P020PCB20AP030_-M01 | Motor | SGW building sump pump motor
P020PCB31AH010_-M01 | TH00P020PCB31AH010_-M01 | Motor | Fin Fan Cooler A Motor 1
P020PCB31AH010_M02 | TH00P020PCB31AH010_M02 | Motor | Fin Fan Cooler A Motor 2
P020PCB31AH010_M03 | TH00P020PCB31AH010_M03 | Motor | Fin Fan Cooler A Motor 3
P020PCB31AH010_M04 | TH00P020PCB31AH010_M04 | Motor | Fin Fan Cooler A Motor 4
P020PCB32AH020_-M01 | TH00P020PCB32AH020_-M01 | Motor | Fin Fan Cooler B Motor 1
P020PCB32AH020_M02 | TH00P020PCB32AH020_M02 | Motor | Fin Fan Cooler B Motor 2
P020PCB32AH020_M03 | TH00P020PCB32AH020_M03 | Motor | Fin Fan Cooler B Motor 3
P020PCB32AH020_M04 | TH00P020PCB32AH020_M04 | Motor | Fin Fan Cooler B Motor 4
P020PCB33AH030_-M01 | TH00P020PCB33AH030_-M01 | Motor | Fin Fan Cooler C Motor 1
P020PCB33AH030_M02 | TH00P020PCB33AH030_M02 | Motor | Fin Fan Cooler C Motor 2
P020PCB33AH030_M03 | TH00P020PCB33AH030_M03 | Motor | Fin Fan Cooler C Motor 3
P020PCB33AH030_M04 | TH00P020PCB33AH030_M04 | Motor | Fin Fan Cooler C Motor 4
P020QFA11AN001_-M01 | TH00P020QFA11AN001_-M01 | Motor | Air compressor motor
S020GAC20AP010_-M01 | TH00S020GAC20AP010_-M01 | Motor | Raw Water Pump A Motor
S020GAC20AP020_-M01 | TH00S020GAC20AP020_-M01 | Motor | Raw Water Pump B Motor
S020GBK10AP010_-M01 | TH00S020GBK10AP010_-M01 | Motor | Calcite inhibitor pump motor
S020GBK10AP020_-M01 | TH00S020GBK10AP020_-M01 | Motor | Calcite inhibitor bund sump pump motor
S020GKA10AP020_-M01 | TH00S020GKA10AP020_-M01 | Motor | Potable water pump B Motor
S020GKA20AP010_-M01 | TH00S020GKA20AP010_-M01 | Motor | Potable Water Pump A Motor
S020GKA20AP020_-M01 | TH00S020GKA20AP020_-M01 | Motor | Potable Water Pump B Motor
S020NDA21AH010_-M01 | TH00S020NDA21AH010_-M01 | Motor | Acid dilution cooler fan A Motor
S020NDA21AP010_-M01 | TH00S020NDA21AP010_-M01 | Motor | ACID DILUTION SGW PUMP (A) Motor
S020NDA21AP020_-M01 | TH00S020NDA21AP020_-M01 | Motor | Acid dilution cooler fan A Motor
S020NDA22AH020_-M01 | TH00S020NDA22AH020_-M01 | Motor | Acid dilution cooler fan B Motor
S020NDA22AP020_-M01 | TH00S020NDA22AP020_-M01 | Motor | ACID DILUTION SGW PUMP (B) Motor
S020QCM20AP010_-M01 | TH00S020QCM20AP010_-M01 | Motor | Acid Dosing Pump A Motor
S020QCM20AP020_-M01 | TH00S020QCM20AP020_-M01 | Motor | Acid dosing pump B Motor
S020QCM21AP020_-M01 | TH00S020QCM21AP020_-M01 | Motor | Acid Dosing Pump B Motor
S020QCM30AP001_-M01 | TH00S020QCM30AP001_-M01 | Motor | Acid dosing sump pump motor
S020QCM30AP001_-M01 | TH00S020QCM30AP001_-M01 | Motor | Acid dosing sump pump motor
TH00
P020NDB10AA110 | TH00P020NDB10AA110 | Motor operated valve | SGW PUMP A OUTLET MOV
P020NDB10AA120 | TH00P020NDB10AA120 | Motor operated valve | SGW PUMP B OUTLET MOV
P020NDB10AA130 | TH00P020NDB10AA130 | Motor operated valve | SGW PUMP C OUTLET MOV
P020NDB10AA140 | TH00P020NDB10AA140 | Motor operated valve | SGW PUMPS BYPASS MOV
L190NDB10AA001 | TH00L190NDB10AA001 | Motor operated valve | SGW CROSS COUNTRY LINE A ISOL MOV
L190NDB10AA002 | TH00L190NDB10AA002 | Motor operated valve | SGW CROSS COUNTRY LINE A MOV
L200NDB10AA001 | TH00L200NDB10AA001 | Motor operated valve | SGW CROSS COUNTRY LINE A MOV
L200NDB10AA002 | TH00L200NDB10AA002 | Motor operated valve | SGW CROSS COUNTRY LINE B MOV
P020NAB10AA030 | TH00P020NAB10AA030 | Motor operated valve | CONDENSATE PUMP A OUTLET MOV
P020NAB10AA110 | TH00P020NAB10AA110 | Motor operated valve | CONDENSATE PUMPS BYPASS MOV
P020LFC20AA010 | TH00P020LFC20AA010 | Motor operated valve | GFHP PUMP A OUTLET MOV
P020LFC20AA020 | TH00P020LFC20AA020 | Motor operated valve | GFHP PUMP B OUTLET MOV
S020NDB10AA053 | TH00S020NDB10AA053 | Motor operated valve | LP MDV OUTLET MOV
S020NDB10AA054 | TH00S020NDB10AA054 | Motor operated valve | LP MDV OUTLET MOV
S020NDB10AA013 | TH00S020NDB10AA013 | Motor operated valve | LP EDV OUTLET MOV
S020NDB10AA023 | TH00S020NDB10AA023 | Motor operated valve | LP EDV OUTLET MOV
S020NDB10AA033 | TH00S020NDB10AA033 | Motor operated valve | LP EDV OUTLET MOV
S020NDA10AA043 | TH00S020NDA10AA043 | Motor operated valve | LP EDV OUTLET MOV
S020NDA30AA020 | TH00S020NDA30AA020 | Motor operated valve | LP SEPARATOR B OUTLET MOV
S020NDB30AA021 | TH00S020NDB30AA021 | Motor operated valve | LP SEPARATOR B OUTLET MOV
S060NDB10AA001 | TH00S060NDB10AA001 | Motor operated valve | LP SEPARATOR OUTLET MOV
L060NDA10AA030 | TH00L060NDA10AA030 | Motor operated valve | TH28 TO HP SEPARATOR MOV
L060NDA10AA040 | TH00L060NDA10AA040 | Motor operated valve | TH28 TO SILENCER MOV
L060NDA10AA050 | TH00L060NDA10AA050 | Motor operated valve | TH12 TO SILENCER MOV
L070NDA10AA030 | TH00L070NDA10AA030 | Motor operated valve | TH26 TO HP SEPARATOR MOV
L070NDA10AA040 | TH00L070NDA10AA040 | Motor operated valve | TH26 TO SILENCER MOV
L050NDA10AA030 | TH00L050NDA10AA030 | Motor operated valve | TH12 TO HP SEPARATOR MOV
L050NDA10AA040 | TH00L050NDA10AA040 | Motor operated valve | TH12 TO SILENCER MOV
S020NAA11AA110 | TH00S020NAA11AA110 | Motor operated valve | HP CDPS MOV | PID0014
S020NAA10AA140 | TH00S020NAA10AA140 | Motor operated valve | HP SCRUBBER MOV | PID0014
S020NAA31AA055 | TH00S020NAA31AA055 | Motor operated valve | LP STEAM SCRUBBING LINE A MOV
S020NAA31AA056 | TH00S020NAA31AA056 | Motor operated valve | LP STEAM SCRUBBING LINE A MOV
S020NAA32AA055 | TH00S020NAA32AA055 | Motor operated valve | LP STEAM SCRUBBING LINE B MOV
S020NAA32AA056 | TH00S020NAA32AA056 | Motor operated valve | LP STEAM SCRUBBING LINE B MOV
S020NAA10AA001 | TH00S020NAA10AA001 | Motor operated valve | HP STEAM SCRUBBING LINE MOV
S020NAA10AA002 | TH00S020NAA10AA002 | Motor operated valve | HP STEAM SCRUBBING LINE MOV
S020NAA20AA001 | TH00S020NAA20AA001 | Motor operated valve | IP STEAM SCRUBBING LINE MOV
S020NAA20AA002 | TH00S020NAA20AA002 | Motor operated valve | IP STEAM SCRUBBING LINE MOV
S020NAA31AA001 | TH00S020NAA31AA001 | Motor operated valve | LP STEAM SCRUBBING LINE A MOV
S020NAA31AA002 | TH00S020NAA31AA002 | Motor operated valve | LP STEAM SCRUBBING LINE A MOV
S020NAA32AA001 | TH00S020NAA32AA001 | Motor operated valve | LP STEAM SCRUBBING LINE B MOV
S020NAA32AA002 | TH00S020NAA32AA002 | Motor operated valve | LP STEAM SCRUBBING LINE B MOV
S020NDA20AA013 | TH00S020NDA20AA013 | Motor operated valve | HP LCV OUTLET MOV
S020NDA20AA023 | TH00S020NDA20AA023 | Motor operated valve | HP LCV OUTLET MOV
S020NDA20AA033 | TH00S020NDA20AA033 | Motor operated valve | HP LCV OUTLET MOV
S020NDA20AA041 | TH00S020NDA20AA041 | Motor operated valve | HP EDV INLET MOV
S020NDA20AA051 | TH00S020NDA20AA051 | Motor operated valve | HP EDV INLET MOV
S020NDA20AA061 | TH00S020NDA20AA061 | Motor operated valve | HP EDV INLET MOV
S020NDA20AA071 | TH00S020NDA20AA071 | Motor operated valve | HP MDV OUTLET MOV
S020NDA20AA072 | TH00S020NDA20AA072 | Motor operated valve | HP MDV OUTLET MOV
S020NDA20AA001 | TH00S020NDA20AA001 | Motor operated valve | HP SEPARATOR OUTLET MOV
S020NDA20AA002 | TH00S020NDA20AA002 | Motor operated valve | HP SEPARATOR OUTLET MOV
S020NDA20AA043 | TH00S020NDA20AA043 | Motor operated valve | HP EDV OUTLET MOV
S020NDA20AA053 | TH00S020NDA20AA053 | Motor operated valve | HP EDV OUTLET MOV
S020NDA20AA063 | TH00S020NDA20AA063 | Motor operated valve | HP EDV OUTLET MOV
S020NDA20AA073 | TH00S020NDA20AA073 | Motor operated valve | HP MDV OUTLET MOV
S020NDA20AA074 | TH00S020NDA20AA074 | Motor operated valve | HP MDV OUTLET MOV
S020NDA30AA010 | TH00S020NDA30AA010 | Motor operated valve | LP SEPARATOR A OUTLET MOV
S020NDA30AA011 | TH00S020NDA30AA011 | Motor operated valve | LP SEPARATOR A OUTLET MOV
S020NDA30AA013 | TH00S020NDA30AA013 | Motor operated valve | IP LCV OUTLET MOV
S020NDA30AA023 | TH00S020NDA30AA023 | Motor operated valve | IP LCV OUTLET MOV
S020NDA30AA033 | TH00S020NDA30AA033 | Motor operated valve | IP LCV OUTLET MOV
S020NDA30AA043 | TH00S020NDA30AA043 | Motor operated valve | IP LCV OUTLET MOV
S020NDA30AA053 | TH00S020NDA30AA053 | Motor operated valve | IP MDV OUTLET MOV
S020NDA30AA054 | TH00S020NDA30AA054 | Motor operated valve | IP MDV OUTLET MOV
S020NDA30AA063 | TH00S020NDA30AA063 | Motor operated valve | IP EDV OUTLET MOV
S020NDA30AA073 | TH00S020NDA30AA073 | Motor operated valve | IP EDV OUTLET MOV
S020NDA30AA083 | TH00S020NDA30AA083 | Motor operated valve | IP EDV OUTLET MOV
S020NDA30AA093 | TH00S020NDA30AA093 | Motor operated valve | IP EDV OUTLET MOV
S020NDA30AA001 | TH00S020NDA30AA001 | Motor operated valve | IP SEPARATOR OUTLET MOV
S020NAA31AA006 | TH00S020NAA31AA006 | Motor operated valve | LP SCRUBBING LINE BYPASS MOV
S020NAA31AA007 | TH00S020NAA31AA007 | Motor operated valve | LP SCRUBBING LINE BYPASS MOV
S020NDB10AA043 | TH00S020NDB10AA043 | Motor operated valve | LP EDV Outlet MOV
S020NDB10AA001 | TH00S020NDB10AA001 | Motor operated valve | LP Separator Outlet MOV
S020NDA30AA021 | TH00S020NDA30AA021 | Motor operated valve | LP Separator B Outlet MOV
S020GAC10AA021 | TH00S020GAC10AA021 | Motor operated valve | RAW WATER SYSTEM MOV
S020GAC10AA031 | TH00S020GAC10AA031 | Motor operated valve | RAW WATER SUPPLY MOV

## Sheet6
TH00L050NDA10AA030 | TABG-JEC-0-000-PRO-PID-0011
TH00L050NDA10AA040 | TABG-JEC-0-000-PRO-PID-0011
TH00L060NDA10AA030 | TABG-JEC-0-000-PRO-PID-0011
TH00L060NDA10AA040 | TABG-JEC-0-000-PRO-PID-0011
TH00L070NDA10AA030 | TABG-JEC-0-000-PRO-PID-0011
TH00L070NDA10AA040 | TABG-JEC-0-000-PRO-PID-0011
TH00S020NDA20AA140 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA001 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA002 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA041 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA043 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA051 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA053 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA061 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA063 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA071 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA072 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA073 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA074 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA013 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA023 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA033 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA140 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA160 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA110 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA120 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA130 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA20AA170 | TABG-JEC-0-000-PRO-PID-0012
TH00S020NDA30AA001 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA002 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA013 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA023 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA033 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA043 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA053 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA054 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA063 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA073 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA083 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA093 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA110 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA120 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA130 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA140 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA150 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA160 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA170 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA180 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NDA30AA190 | TABG-JEC-0-000-PRO-PID-0013
TH00S020NAA31AA006 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NAA31AA007 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDA30AA010 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDA30AA011 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDA30AA020 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDA30AA021 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA001 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA013 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA023 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA033 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA043 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA053 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA110 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA120 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA130 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA140 | TABG-JEC-0-000-PRO-PID-0014
TH00S020NDB10AA150 | TABG-JEC-0-000-PRO-PID-0014
TH00V010NAA10AA111 | TABG-JEC-0-000-PRO-PID-0016
TH00V010NAA10AA121 | TABG-JEC-0-000-PRO-PID-0016
TH00V010NAA10AA131 | TABG-JEC-0-000-PRO-PID-0016
TH00V010NAA20AA111 | TABG-JEC-0-000-PRO-PID-0016
TH00V010NAA20AA121 | TABG-JEC-0-000-PRO-PID-0016
TH00S020NAA31AA055 | TABG-JEC-0-000-PRO-PID-0017
TH00S020NAA31AA056 | TABG-JEC-0-000-PRO-PID-0017
TH00S020NAA32AA055 | TABG-JEC-0-000-PRO-PID-0017
TH00S020NAA32AA056 | TABG-JEC-0-000-PRO-PID-0017
TH00V010NAA40AA111 | TABG-JEC-0-000-PRO-PID-0017
TH00V010NAA40AA121 | TABG-JEC-0-000-PRO-PID-0017
TH00V010NAA40AA131 | TABG-JEC-0-000-PRO-PID-0017
TH00V010NAA40AA141 | TABG-JEC-0-000-PRO-PID-0017
TH00S020LCE10AA110 | TABG-JEC-0-000-PRO-PID-0018
TH00S020NAA10AA001 | TABG-JEC-0-000-PRO-PID-0019
TH00S020NAA10AA002 | TABG-JEC-0-000-PRO-PID-0019
TH00S020NAA11AA101 | TABG-JEC-0-000-PRO-PID-0019
TH00S020LCE10AA120 | TABG-JEC-0-000-PRO-PID-0020
TH00S020NAA20AA001 | TABG-JEC-0-000-PRO-PID-0021
TH00S020NAA20AA002 | TABG-JEC-0-000-PRO-PID-0021
TH00S020LCE10AA130 | TABG-JEC-0-000-PRO-PID-0022
TH00S020NAA31AA001 | TABG-JEC-0-000-PRO-PID-0023
TH00S020NAA31AA002 | TABG-JEC-0-000-PRO-PID-0023
TH00S020LCE10AA140 | TABG-JEC-0-000-PRO-PID-0024
TH00S020NAA32AA001 | TABG-JEC-0-000-PRO-PID-0025
TH00S020NAA32AA002 | TABG-JEC-0-000-PRO-PID-0025
TH00L190NDB10AA001 | TABG-JEC-0-000-PRO-PID-0026
TH00L190NDB10AA002 | TABG-JEC-0-000-PRO-PID-0026
TH00L200NDB10AA001 | TABG-JEC-0-000-PRO-PID-0026
TH00L200NDB10AA002 | TABG-JEC-0-000-PRO-PID-0026
TH00P020NDB10AA110 | TABG-JEC-0-000-PRO-PID-0026
TH00P020NDB10AA120 | TABG-JEC-0-000-PRO-PID-0026
TH00P020NDB10AA130 | TABG-JEC-0-000-PRO-PID-0026
TH00P020NDB10AA140 | TABG-JEC-0-000-PRO-PID-0026
TH00P020LFC20AA010 | TABG-JEC-0-000-PRO-PID-0028
TH00P020LFC20AA020 | TABG-JEC-0-000-PRO-PID-0028
TH00P020LFC20AA110 | TABG-JEC-0-000-PRO-PID-0028
TH00P020NAB10AA110 | TABG-JEC-0-000-PRO-PID-0028
TH00P020NAB10AA030 | TABG-JEC-0-000-PRO-PID-0028
TH00P020NAB10AA031 | TABG-JEC-0-000-PRO-PID-0028
TH00S020QCM21AA015 | TABG-JEC-0-000-PRO-PID-0030
TH000280NDA10AA110 | TABG-JEC-0-000-PRO-PID-0031
TH000340NDA10AA110 | TABG-JEC-0-000-PRO-PID-0031
TH000290NDB10AA012 | TABG-JEC-0-000-PRO-PID-0032
TH000290NDB10AA110 | TABG-JEC-0-000-PRO-PID-0032
TH000310NDB10AA012 | TABG-JEC-0-000-PRO-PID-0032
TH000310NDB10AA110 | TABG-JEC-0-000-PRO-PID-0032
TH00EA30NDB10AA012 | TABG-JEC-0-000-PRO-PID-0032
TH00EA30NDB10AA110 | TABG-JEC-0-000-PRO-PID-0032
TH000110NAB10AA110 | TABG-JEC-0-000-PRO-PID-0033
TH00L190NDB10AA011 | TABG-JEC-0-000-PRO-PID-0035
TH00L190NDB10AA012 | TABG-JEC-0-000-PRO-PID-0035
TH00L190NDB10AA015 | TABG-JEC-0-000-PRO-PID-0035
TH00L190NDB10AA016 | TABG-JEC-0-000-PRO-PID-0035
TH00L190NDB10AA021 | TABG-JEC-0-000-PRO-PID-0035
TH00L190NDB10AA022 | TABG-JEC-0-000-PRO-PID-0035
TH00L190NDB10AA031 | TABG-JEC-0-000-PRO-PID-0035
TH00L190NDB10AA032 | TABG-JEC-0-000-PRO-PID-0035
TH00L190NDB10AA035 | TABG-JEC-0-000-PRO-PID-0035
TH00L190NDB10AA036 | TABG-JEC-0-000-PRO-PID-0035
TH00L200NDB10AA011 | TABG-JEC-0-000-PRO-PID-0035
TH00L200NDB10AA012 | TABG-JEC-0-000-PRO-PID-0035
TH00L200NDB10AA021 | TABG-JEC-0-000-PRO-PID-0035
TH00L200NDB10AA022 | TABG-JEC-0-000-PRO-PID-0035
TH000260NDA10AA110 | TABG-JEC-0-000-PRO-PID-0036
TH000300NDA10AA110 | TABG-JEC-0-000-PRO-PID-0036
TH000120NDA10AA110 | TABG-JEC-0-000-PRO-PID-0037
TH000210NDA10AA110 | TABG-JEC-0-000-PRO-PID-0037
TH000330NDB10AA012 | TABG-JEC-0-000-PRO-PID-0038
TH000330NDB10AA110 | TABG-JEC-0-000-PRO-PID-0038
TH000320NDB10AA012 | TABG-JEC-0-000-PRO-PID-0038
TH000320NDB10AA110 | TABG-JEC-0-000-PRO-PID-0038
TH001910NDB10AA012 | TABG-JEC-0-000-PRO-PID-0039
TH001910NDB10AA110 | TABG-JEC-0-000-PRO-PID-0039
TH001920NDB10AA012 | TABG-JEC-0-000-PRO-PID-0039
TH001920NDB10AA110 | TABG-JEC-0-000-PRO-PID-0039
TH001930NDB10AA012 | TABG-JEC-0-000-PRO-PID-0039
TH001930NDB10AA110 | TABG-JEC-0-000-PRO-PID-0039