## Sheet1
Station | System | Tag | Point | Funct | Type | Criticality | ResCon | PECPR | KPI | NominalValue | Setting | Range | DeviceType | Proof | PlantCode | Data | StoresNo | DrawingNo | Procs | MVUnit | IdealUnit | MVar1 | MVar2 | MVar3 | MVar4 | MVar5 | MVar6 | MVar7 | IdO1 | IdO2 | IdO3 | IdO4 | IdO5 | IdO6 | IdO7 | Digi1 | Digi2 | Digi3 | Digi4 | Digi5 | Digi6 | DigiAliase1 | DigiAliase2 | DigiAliase3 | DigiAliase4 | DigiAliase5 | DigiAliase6 | DateChecked | CheckedBy
Tauhara B Steamfield | Wellpad TH11 Common Steam/Water Dump System | 10CL010 | Wellpad TH11 | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | C |  |  |  | - | 2200 to 6000 | 2200 to 6000 | Level Transmitter (Radar) |  | 0110LFC10CL010 | CCI-DAT-1468 | TBC | PRO-PID-33 | TH11-7.5.001-01 | mm | mA | MVar1: 2200; MVar2: 3150; MVar3: 4100; MVar4: 5050; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 500
Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CF010 | Wellpad TH11 | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B |  |  |  | 550 | -10 to 1500 | 0 to 1500 | Flow Transmitter (Orifice Flow) |  | 0110NAB10CF010 | CCI-DAT-1472 | TBC | PRO-PID-33 | TH11-7.5.001-01 | tph | mA | MVar1: 0; MVar2: 375; MVar3: 750; MVar4: 1125; MVar5: 1500; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CP010 | Wellpad TH11 | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B |  |  |  | 5.1 | -1 to 55 | 0 to 25 | Pressure Indicating Transmitter |  | 0110NAB10CP010 | PRO-CAL-0039 | TBC | PRO-PID-33 | TH11-7.5.001-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 20
Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CP510 | Wellpad TH11 | TBC | Wika 72039878+14503369+0731277 | C |  |  |  | 5.1 | 0 to 25 | - | Pressure Gauge |  | 0110NAB10CP510 | CCI-DAT-1461 | TBC | PRO-PID-33 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 0; IdO2: 6.25; IdO3: 12.5; IdO4: 18.75; IdO5: 25
Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CP520 | Wellpad TH11 | TBC | Wika 72039878+14503369+0731277 | C |  |  |  | 5.1 | 0 to 25 | - | Pressure Gauge |  | 0110NAB10CP520 | CCI-DAT-1460 | TBC | PRO-PID-33 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 0; IdO2: 6.25; IdO3: 12.5; IdO4: 18.75; IdO5: 25
Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CL010 | Wellpad TH12 | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | C |  |  |  | 950 | 0 to 1300 | 0 to 1300 | Level Transmitter (Radar) |  | 0120LFC10CL010 | CCI-DAT-1460 | TBC | PRO-PID-37 | TH12-8.5.002-01 | mm | mA | MVar1: 0; MVar2: 325; MVar3: 650; MVar4: 975; MVar5: 1300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CL020 | Wellpad TH12 | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | 2350 | 2200 to 6000 | 2200 to 6000 | Level Transmitter (Radar) |  | 0120LFC10CL020 | CCI-DAT-1468 | TBC | PRO-PID-37 | TH12-8.5.001-01 | mm | mA | MVar1: 2200; MVar2: 3150; MVar3: 4100; MVar4: 5050; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 500
Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CP010 | Wellpad TH12 | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | C |  |  |  | 0 | -1 to 10.3 | 0 to 10 | Pressure Indicating Transmitter |  | 0120LFC10CP010 | CCI-DAT-1468 | TBC | PRO-PID-37 | TH12-8.5.002-01 | bar(g) | mA | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CP510 | Wellpad TH12 | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0120LFC10CP510 | CCI-DAT-1461 | TBC | PRO-PID-37 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CF010 | Wellpad TH12 | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B |  |  |  | 699 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0120NDA10CF010 | CCI-DAT-1460 | TBC | PRO-PID-37 | TH12-8.5.001-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CF020 | Wellpad TH12 | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | C |  |  |  | 699 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0120NDA10CF020 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-37 | TH12-8.5.001-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CP010 | Wellpad TH12 | TBC | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B |  |  |  | 0 | -1 to 276 | 0 to 75 | Pressure Indicating Transmitter |  | 0120NDA10CP010 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-37 | TH12-8.5.001-01 | bar(g) | mA | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 70
Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CP510 | Wellpad TH12 | TBC | Wika 72039884+14503369+0763349 | C |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0120NDA10CP510 | CCI-DAT-1461 | TBC | PRO-PID-37 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CP520 | Wellpad TH12 | TBC | Wika 72039884+14503369+0763349 | C |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0120NDA10CP520 | CCI-DAT-1460 | TBC | PRO-PID-37 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CT010 | Wellpad TH12 | TBC | Rosemount 644HANAJ1M4Q4T1 | C |  |  |  | 235 | 0 to 300 | 0 to 300 | Temperature Indicating Transmitter |  | 0120NDA10CT010 | CCI-DAT-1460 | TBC | PRO-PID-37 | TH12-8.5.001-01 | °C | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CF010 | Wellpad TH12 (TH21) | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B |  |  |  | 699 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0210NDA10CF010 | CCI-DAT-1465 | TBC | PRO-PID-37 | TH12-8.5.002-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CF020 | Wellpad TH12 (TH21) | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | - |  |  |  | 699 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0210NDA10CF020 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-37 | TH12-8.5.002-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CP010 | Wellpad TH12 (TH21) | TBC | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B |  |  |  | 30 | -1 to 276 | 0 to 75 | Pressure Indicating Transmitter |  | 0210NDA10CP010 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-37 | TH12-8.5.002-01 | bar(g) | mA | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 70
Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CP510 | Wellpad TH12 (TH21) | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0210NDA10CP510 | CCI-DAT-1461 | TBC | PRO-PID-37 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CP520 | Wellpad TH12 (TH21) | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0210NDA10CP520 | CCI-DAT-1460 | TBC | PRO-PID-37 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CT010 | Wellpad TH12 (TH21) | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 235 | 0 to 300 | 0 to 300 | Temperature Indicating Transmitter |  | 0210NDA10CT010 | CCI-DAT-1460 | TBC | PRO-PID-37 | TH12-8.5.002-01 | °C | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CL010 | Wellpad TH26 | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | 950 | 0 to 1300 | 0 to 1300 | Level Transmitter (Radar) |  | 0260LFC10CL010 | CCI-DAT-1465 | TBC | PRO-PID-36 | TH26-4.5.002-01 | mm | mA | MVar1: 0; MVar2: 325; MVar3: 650; MVar4: 975; MVar5: 1300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CL020 | Wellpad TH26 | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | 2350 | 2200 to 6000 | 2200 to 6000 | Level Transmitter (Radar) |  | 0260LFC10CL020 | CCI-DAT-1468 | TBC | PRO-PID-36 | TH26-4.5.001-01 | mm | mA | MVar1: 2200; MVar2: 3150; MVar3: 4100; MVar4: 5050; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 500
Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CP010 | Wellpad TH26 | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 0 | -1 to 10.3 | 0 to 10 | Pressure Indicating Transmitter |  | 0260LFC10CP010 | CCI-DAT-1468 | TBC | PRO-PID-36 | TH26-4.5.002-01 | bar(g) | mA | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CP510 | Wellpad TH26 | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0260LFC10CP510 | CCI-DAT-1461 | TBC | PRO-PID-36 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CF010 | Wellpad TH26 | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B |  |  |  | 699 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0260NDA10CF010 | CCI-DAT-1460 | TBC | PRO-PID-36 | TH26-4.5.001-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CF020 | Wellpad TH26 | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | - |  |  |  | 699 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0260NDA10CF020 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-36 | TH26-4.5.001-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CP010 | Wellpad TH26 | TBC | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B |  |  |  | 0 | -1 to 276 | 0 to 75 | Pressure Indicating Transmitter |  | 0260NDA10CP010 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-36 | TH26-4.5.001-01 | bar(g) | mA | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 70
Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CP510 | Wellpad TH26 | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0260NDA10CP510 | CCI-DAT-1461 | TBC | PRO-PID-36 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CP520 | Wellpad TH26 | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0260NDA10CP520 | CCI-DAT-1460 | TBC | PRO-PID-36 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CT010 | Wellpad TH26 | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 235 | 0 to 300 | 0 to 300 | Temperature Indicating Transmitter |  | 0260NDA10CT010 | CCI-DAT-1460 | TBC | PRO-PID-36 | TH26-4.5.001-01 | °C | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump System | 10CL010 | Wellpad TH28 | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | 950 | 0 to 1300 | 0 to 1300 | Level Transmitter (Radar) |  | 0280LFC10CL010 | CCI-DAT-1465 | TBC | PRO-PID-31 | TH28-9.5.002-01 | mm | mA | MVar1: 0; MVar2: 325; MVar3: 650; MVar4: 975; MVar5: 1300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump System | 10CL020 | Wellpad TH28 | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | 2350 | 2200 to 6000 | 2200 to 6000 | Level Transmitter (Radar) |  | 0280LFC10CL020 | CCI-DAT-1468 | TBC | PRO-PID-31 | TH28-9.5.001-01 | mm | mA | MVar1: 2200; MVar2: 3150; MVar3: 4100; MVar4: 5050; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 500
Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump System | 10CP510 | Wellpad TH28 | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0280LFC10CP510 | CCI-DAT-1468 | TBC | PRO-PID-31 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CF010 | Wellpad TH28 | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B |  |  |  | 531 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0280NDA10CF010 | CCI-DAT-1460 | TBC | PRO-PID-31 | TH28-9.5.001-01 | - | mA | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CF020 | Wellpad TH28 | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | - |  |  |  | 531 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0280NDA10CF020 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-31 | TH28-9.5.003-01 | - | mA | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CP010 | Wellpad TH28 | TBC | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B |  |  |  | 26.3 | -1 to 276 | 0 to 75 | Pressure Indicating Transmitter |  | 0280NDA10CP010 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-31 | TH28-9.5.001-01 | bar(g) | mA | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 70
Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CP510 | Wellpad TH28 | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 26.3 | 0 to 100 | - | Pressure Gauge |  | 0280NDA10CP510 | CCI-DAT-1461 | TBC | PRO-PID-31 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CP520 | Wellpad TH28 | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 20.5 | 0 to 100 | - | Pressure Gauge |  | 0280NDA10CP520 | CCI-DAT-1460 | TBC | PRO-PID-31 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CT010 | Wellpad TH28 | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 216 | 0 to 300 | 0 to 300 | Temperature Indicating Transmitter |  | 0280NDA10CT010 | CCI-DAT-1460 | TBC | PRO-PID-31 | TH28-9.5.001-01 | °C | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH29 Common Steam/Water Dump System | 10CL010 | Wellpad TH29 | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | - | 2200 to 6000 | 2200 to 6000 | Level Transmitter (Radar) |  | 0290LFC10CL010 | CCI-DAT-1465 | TBC | PRO-PID-32 | TH29-2.5.001-01 | mm | mA | MVar1: 2200; MVar2: 3150; MVar3: 4100; MVar4: 5050; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 500
Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CF010 | Wellpad TH29 | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 550 | -5 to 605 | 0 to 900 | Flow Transmitter (Orifice Flow) |  | 0290NDB10CF010 | CCI-DAT-1468 | TBC | PRO-PID-32 | TH29-2.5.001-01 | tph | mA | MVar1: -; MVar2: -; MVar3: -; MVar4: -; MVar5: -; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CP010 | Wellpad TH29 | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 15 | -1 to 55 | 0 to 50 | Pressure Indicating Transmitter |  | 0290NDB10CP010 | CCI-DAT-1472 | TBC | PRO-PID-32 | TH29-2.5.001-01 | bar(g) | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CP510 | Wellpad TH29 | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0290NDB10CP510 | PRO-CAL-0039 | TBC | PRO-PID-32 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CP520 | Wellpad TH29 | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0290NDB10CP520 | CCI-DAT-1461 | TBC | PRO-PID-32 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CF010 | Wellpad TH26 (TH30) | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B |  |  |  | 699 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0300NDA10CF010 | CCI-DAT-1460 | TBC | PRO-PID-36 | TH26-4.5.002-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CF020 | Wellpad TH26 (TH30) | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | - |  |  |  | 699 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0300NDA10CF020 | CCI-DAT-1460 | TBC | PRO-PID-36 | TH26-4.5.002-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 192.5; MVar3: 385; MVar4: 577.5; MVar5: 770; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CP010 | Wellpad TH26 (TH30) | TBC | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B |  |  |  | 30 | -1 to 276 | 0 to 75 | Pressure Indicating Transmitter |  | 0300NDA10CP010 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-36 | TH26-4.5.002-01 | bar(g) | mA | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 70
Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CP510 | Wellpad TH26 (TH30) | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0300NDA10CP510 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-36 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CP520 | Wellpad TH26 (TH30) | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 30 | 0 to 100 | - | Pressure Gauge |  | 0300NDA10CP520 | CCI-DAT-1461 | TBC | PRO-PID-36 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CT010 | Wellpad TH26 (TH30) | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 235 | 0 to 300 | 0 to 300 | Temperature Indicating Transmitter |  | 0300NDA10CT010 | CCI-DAT-1460 | TBC | PRO-PID-36 | TH26-4.5.002-01 | °C | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CF010 | Wellpad TH29 (TH31) | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B |  |  |  | 550 | -5 to 605 | 0 to 1400 | Flow Transmitter (Orifice Flow) |  | 0310NDB10CF010 | CCI-DAT-1460 | TBC | PRO-PID-32 | TH29-2.5.002-01 | tph | mA | MVar1: 0; MVar2: 100; MVar3: 200; MVar4: 300; MVar5: 400; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CP010 | Wellpad TH29 (TH31) | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B |  |  |  | 15 | -1 to 55 | 0 to 50 | Pressure Indicating Transmitter |  | 0310NDB10CP010 | CCI-DAT-1465 | TBC | PRO-PID-32 | TH29-2.5.002-01 | bar(g) | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 45
Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CP501 | Wellpad TH29 (TH31) | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0310NDB10CP501 | CCI-DAT-1472 | TBC | PRO-PID-32 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CP520 | Wellpad TH29 (TH31) | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0310NDB10CP520 | PRO-CAL-0039 | TBC | PRO-PID-32 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CF010 | Wellpad TH28 (TH34) | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B |  |  |  | 531 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0360NDA10CF010 | CCI-DAT-1461 | TBC | PRO-PID-31 | TH28-9.5.002-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 147.5; MVar3: 295; MVar4: 442.5; MVar5: 590; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CF020 | Wellpad TH28 (TH34) | TBC | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | - |  |  |  | 531 | TBC | TBC | Flow Transmitter (Orifice Flow) |  | 0360NDA10CF020 | CCI-DAT-1460 | TBC | PRO-PID-31 | TH28-9.5.002-01 | tph (Note 1) | mA | MVar1: 0; MVar2: 147.5; MVar3: 295; MVar4: 442.5; MVar5: 590; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CP010 | Wellpad TH28 (TH34) | TBC | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | - |  |  |  | 26.3 | -1 to 276 | 0 to 75 | Pressure Indicating Transmitter |  | 0360NDA10CP010 | CCI-DAT-1460 | TBC | PRO-PID-31 | TH28-9.5.002-01 | bar(g) | mA | MVar1: 0; MVar2: 18.75; MVar3: 37.5; MVar4: 56.25; MVar5: 75; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 70
Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CP510 | Wellpad TH28 (TH34) | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 26.3 | 0 to 100 | - | Pressure Gauge |  | 0360NDA10CP510 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-31 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CP520 | Wellpad TH28 (TH34) | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 20.5 | 0 to 100 | - | Pressure Gauge |  | 0360NDA10CP520 | CCI-DAT-1472 Note 2 | TBC | PRO-PID-31 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 0; IdO2: 25; IdO3: 50; IdO4: 75; IdO5: 100
Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CT010 | Wellpad TH28 (TH34) | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 216 | 0 to 300 | 0 to 300 | Temperature Indicating Transmitter |  | 0360NDA10CT010 |  | TBC | PRO-PID-31 | TH28-9.5.002-01 | °C | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH29 (TH35) Separated Water System | 10CF010 | Wellpad TH29 (TH35) | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B |  |  |  | 15 | -5 to 605 | -5 to 200 | Flow Transmitter (Orifice Flow) |  | 0350NDB10CF010 | CCI-DAT-1460 | TBC | PRO-PID-32 | TH29-2.5-003-01 | tph | mA | MVar1: -5; MVar2: 46.25; MVar3: 97.5; MVar4: 148.75; MVar5: 200; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH29 (TEA-3) Separated Water System | 10CP010 | Wellpad TH29 (TEA-3) | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B |  |  |  | 30 | -1 to 55 | 0 to 50 | Pressure Indicating Transmitter |  | 0350NDB10CP010 | CCI-DAT-1460 | TBC | PRO-PID-32 | TH29-2.5-003-01 | bar(g) | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 45
Tauhara B Steamfield | Wellpad TH29 (TH35) Separated Water System | 10CP510 | Wellpad TH29 (TH35) | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 30 | 0 to 60 | - | Pressure Gauge |  | 0350NDB10CP510 | CCI-DAT-1465 | TBC | PRO-PID-32 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad TH29 (TH35) Separated Water System | 10CP520 | Wellpad TH29 (TH35) | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0350NDB10CP520 | CCI-DAT-1472 | TBC | PRO-PID-32 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CF010 | Wellpad TH37 | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B |  |  |  | 370 | 0 to 1000 | 0 to 1000 | Flow Transmitter (Orifice Flow) |  | 0370NDB10CF010 | PRO-CAL-0039 | TBC | PRO-PID-38 | TAS1-3.5.001-01 | tph | mA | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CP010 | Wellpad TH37 | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B |  |  |  | 15 | -1 to 55 | 0 to 50 | Pressure Indicating Transmitter |  | 0370NDB10CP010 | CCI-DAT-1461 | TBC | PRO-PID-38 | TAS1-3.5.001-01 | bar(g) | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 45
Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CP510 | Wellpad TH37 | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0370NDB10CP510 | CCI-DAT-1460 | TBC | PRO-PID-38 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CP520 | Wellpad TH37 | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0370NDB10CP520 | CCI-DAT-1460 | TBC | PRO-PID-38 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CF010 | Wellpad TH37/38 | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B |  |  |  | 370 | 0 to 1000 | 0 to 1000 | Flow Transmitter (Orifice Flow) |  | 0380NDB10CF010 | CCI-DAT-1472 | TBC | PRO-PID-38 | TAS1-3.5.002-01 | tph | mA | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CP010 | Wellpad TH37/38 | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B |  |  |  | 15 | -1 to 55 | 0 to 50 | Pressure Indicating Transmitter |  | 0380NDB10CP010 | PRO-CAL-0039 | TBC | PRO-PID-38 | TAS1-3.5.002-01 | bar(g) | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 45
Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CP501 | Wellpad TH37/38 | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0380NDB10CP501 | CCI-DAT-1461 | TBC | PRO-PID-38 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CP520 | Wellpad TH37/38 | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0380NDB10CP520 | CCI-DAT-1460 | TBC | PRO-PID-38 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CP010 | TH12 Two Phase Pipeline | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 21.27 | -1 to 55 | 0 to 35 | Pressure Indicating Transmitter |  | L050NDA10CP010 | CCI-DAT-1460 | TBC | PRO-PID-11 | TAS2-205-01 | bar(g) | mA | MVar1: 0; MVar2: 8.75; MVar3: 17.5; MVar4: 26.25; MVar5: 35; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 20
Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CP532 | TH12 Two Phase Pipeline | TBC | Wika 72039883+14503369+0763349 | - |  |  |  | 25 | 0 to 40 | - | Pressure Gauge |  | L050NDA10CP532 | CCI-DAT-1472 | TBC | PRO-PID-37 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40; IdO1: 0; IdO2: 10; IdO3: 20; IdO4: 30; IdO5: 40
Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CT010 | TH12 Two Phase Pipeline | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 217.9 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | L050NDA10CT010 | PRO-CAL-0039 | TBC | PRO-PID-11 | TAS2-205-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CT030 | TH12 Two Phase Pipeline | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 215 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | L050NDA10CT030 | CCI-DAT-1461 | TBC | PRO-PID-37 | TH12-8.5.001-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CP010 | TH28 Two Phase Pipeline | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 21.27 | -1 to 55 | 0 to 35 | Pressure Indicating Transmitter |  | L060NDA10CP010 | CCI-DAT-1460 | TBC | PRO-PID-11 | TAS2-105-01 | bar(g) | mA | MVar1: 0; MVar2: 8.75; MVar3: 17.5; MVar4: 26.25; MVar5: 35; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 20
Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CP532 | TH28 Two Phase Pipeline | TBC | Wika 72039884+14503369+0763349 | - |  |  |  | 20.5 | -1 to 55 | 0 to 50 | Pressure Gauge |  | L060NDA10CP532 | CCI-DAT-1460 | TBC | PRO-PID-31 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 0; IdO2: 12.5; IdO3: 25; IdO4: 37.5; IdO5: 50
Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT010 | TH28 Two Phase Pipeline | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 217.9 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | L060NDA10CT010 | CCI-DAT-1461 | TBC | PRO-PID-11 | TAS2-105-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT030 | TH28 Two Phase Pipeline | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 216 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | L060NDA10CT030 | CCI-DAT-1460 | TBC | PRO-PID-31 | TH28-9.5.001-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT510 | TH28 Two Phase Pipeline | TBC | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - |  |  |  | 215 | 0 to 250 | - | Temperature Indicator (Gauge) |  | L060NDA10CT510 | CCI-DAT-1465 | TBC | PRO-PID-34 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT511 | TH28 Two Phase Pipeline | TBC | Wika 72039935 Model S5550)+72039932 (Model TW15-H) | - |  |  |  | 215 | 0 to 250 | - | Temperature Indicator (Gauge) |  | L060NDA10CT511 | CCI-DAT-1465 | TBC | PRO-PID-34 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT520 | TH28 Two Phase Pipeline | TBC | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - |  |  |  | 215 | 0 to 250 | - | Temperature Indicator (Gauge) |  | L060NDA10CT520 | CCI-DAT-1461 | TBC | PRO-PID-34 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT521 | TH28 Two Phase Pipeline | TBC | Wika 72040072 (Model S5550/4) +72040071 (TW15-H) | - |  |  |  | 215 | 0 to 250 | - | Temperature Indicator (Gauge) |  | L060NDA10CT521 | CCI-DAT-1460 | TBC | PRO-PID-34 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | TH26 Two Phase Pipeline Common Steam/Water Dump System | 10CL010 | TH26 Two Phase Pipeline | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | - | 2200 to 6000 | 2200 to 6000 | Level Transmitter (Radar) |  | L070LFC10CL010 | CCI-DAT-1465 | TBC | PRO-PID-34 | TH28-9.5.001-01 | mm | mA | MVar1: 2200; MVar2: 3150; MVar3: 4100; MVar4: 5050; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 500
Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CP010 | TH26 Two Phase Pipeline | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 21.27 | -1 to 55 | 0 to 35 | Pressure Indicating Transmitter |  | L070NDA10CP010 | CCI-DAT-1465 | TBC | PRO-PID-11 | TAS2-105-01 | bar(g) | mA | MVar1: 0; MVar2: 8.75; MVar3: 17.5; MVar4: 26.25; MVar5: 35; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 20
Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CP532 | TH26 Two Phase Pipeline | TBC | Wika 72039883+14503369+0763349 | - |  |  |  | 25 | 0 to 40 | - | Pressure Gauge |  | L070NDA10CP532 | CCI-DAT-1463 | TBC | PRO-PID-36 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40; IdO1: 0; IdO2: 10; IdO3: 20; IdO4: 30; IdO5: 40
Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT010 | TH26 Two Phase Pipeline | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 217.9 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | L070NDA10CT010 | CCI-DAT-1463 | TBC | PRO-PID-11 | TAS2-105-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT030 | TH26 Two Phase Pipeline | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 215 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | L070NDA10CT030 | CCI-DAT-1463 | TBC | PRO-PID-36 | TH26-4.5.001-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT510 | TH26 Two Phase Pipeline | TBC | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - |  |  |  | 215 | 0 to 250 | - | Temperature Indicator (Gauge) |  | L070NDA10CT510 | CCI-DAT-1463 | TBC | PRO-PID-34 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT511 | TH26 Two Phase Pipeline | TBC | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - |  |  |  | 215 | 0 to 250 | - | Temperature Indicator (Gauge) |  | L070NDA10CT511 | CCI-DAT-1468 | TBC | PRO-PID-34 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT512 | TH26 Two Phase Pipeline | TBC | Wika 72039935 Model S5550)+72039932 (Model TW15-H) | - |  |  |  | 215 | 0 to 250 | - | Temperature Indicator (Gauge) |  | L070NDA10CT512 | CCI-DAT-1461 | TBC | PRO-PID-34 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT522 | TH26 Two Phase Pipeline | TBC | Wika 72040072 (Model S5550/4) +72040071 (TW15-H) | - |  |  |  | 215 | 0 to 250 | - | Temperature Indicator (Gauge) |  | L070NDA10CT522 | CCI-DAT-1460 | TBC | PRO-PID-34 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | Condensate Pipeline To TH11 Condensate System | 10CP510 | Condensate Pipeline To TH11 | TBC | Wika 72039879+14503369+0731277 | - |  |  |  | 5 | 0 to 16 | - | Pressure Gauge |  | L150NAB10CP510 | CCI-DAT-1465 | TBC | PRO-PID-33 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | SGW Pipeline To TH29 Well Pad Separated Water System | 10CP010 | SGW Pipeline To TH29 Well Pad | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 30 | -1 to 55 | -1 to 50 | Pressure Indicating Transmitter |  | L190NDB10CP010 | CCI-DAT-1465 | TBC | PRO-PID-35 | TAS1-3.5.001-01 | bar(g) | mA | MVar1: -1; MVar2: 11.75; MVar3: 24.5; MVar4: 37.25; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water System | 10CP011 | SWG Pipeline to TH29 Wellpad | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 15 | -1 to 55 | 0 to 50 | Pressure Indicating Transmitter |  | L190NDB10CP011 | CCI-DAT-1463 | TBC | PRO-PID-32 | TH29-2.5.001-01 | bar(g) | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water System | 10CP510 | SWG Pipeline to TH29 Wellpad | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | L190NDB10CP510 | CCI-DAT-1463 | TBC | PRO-PID-32 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water System | 10CT010 | SWG Pipeline to TH29 Wellpad | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 123 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | L190NDB10CT010 | CCI-DAT-1463 | TBC | PRO-PID-32 | TH29-2.5.001-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SGW Pipeline To TH19N Separated Water System | 10CP010 | SGW Pipeline To TH19N | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 30 | -1 to 55 | -1 to 50 | Pressure Indicating Transmitter |  | L200NDB10CP010 | CCI-DAT-1463 | TBC | PRO-PID-35 | TAS1-3.5.001-01 | bar(g) | mA | MVar1: -1; MVar2: 11.75; MVar3: 24.5; MVar4: 37.25; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SGW Pipeline To Wellpad LCP Separated Water System | 10CP510 | SGW Pipeline To Wellpad LCP | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | L210NDB10CP510 | CCI-DAT-1460 | TBC | PRO-PID-38 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | SGW Pipeline To Wellpad LCP Separated Water System | 10CT010 | SGW Pipeline To Wellpad LCP | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 123 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | L210NDB10CT010 | CCI-DAT-1461 | TBC | PRO-PID-38 | TAS1-3.5.001-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH37 Common Steam/Water Dump System | 10CL010 | Wellpad TH37 | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | - | 2200 to 6000 | 2200 to 6000 | Level Transmitter (Radar) |  | 0370LFC10CL010 | CCI-DAT-1461 | TBC | PRO-PID-38 | TAS1-3.5-001-01 | mm | mA | MVar1: 2200; MVar2: 3150; MVar3: 4100; MVar4: 5050; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 500
Tauhara B Steamfield | Pump Station Seal Water System | 20CL010 | Pump Station | TBC | Rosemount 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8 | - |  |  |  | N/A | Note 9 | Note 9 | Level Transmitter (Radar) |  | P020GWA20CL010 | CCI-DAT-1460 | TBC | PRO-PID-41 | TAS3-105-01 | mm | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 20CL011 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | N/A | Note 9 | Refer to Notes | Level Gauge |  | P020GAC20CL011 | CCI-DAT-1465 | TBC | PRO-PID-41 | 0 | mm | mm | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Pump Station Seal Water System | 20CL020 | Pump Station | TBC | Rosemount 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8 | - |  |  |  | N/A | Note 9 | Note 9 | Level Transmitter (Radar) |  | P020GWA20CL020 | CCI-DAT-1461 | TBC | PRO-PID-41 | TAS3-205-01 | mm | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 20CL021 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | N/A | Note 9 | Refer to Notes | Level Gauge |  | P020GAC20CL021 | CCI-DAT-1460 | TBC | PRO-PID-41 | 0 | mm | mm | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Pump Station Potable Water System | 21CP520 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 3.49 | -1 to 55 | 0 to 10 | Pressure Indicating Transmitter |  | S020GKA21CP520 | CCI-DAT-1465 | TBC | PRO-PID-40 | TAS2-111-01 | bar(g) | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 15 |  | 5
Tauhara B Steamfield | Pump Station Seal Water System | 20CP510 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GAC20CP510 | CCI-DAT-1468 | TBC | PRO-PID-41 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 20CP511 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GAC20CP511 | CCI-DAT-1468 | TBC | PRO-PID-41 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 30CP590 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GAC30CP590 | CCI-DAT-1471 | TBC | PRO-PID-41 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 30CP591 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GAC30CP591 | CCI-DAT-1468 | TBC | PRO-PID-41 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 30CT050 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 32 | 0 to 250 | 0 to 250 | Temperature Element |  | P020GWA30CT050 | CCI-DAT-1471 | TBC | PRO-PID-41 | TAS3-101-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 40
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CL010 | Pump Station | TBC | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - |  |  |  | 773 | TBC | TBC | Level Transmitter (DP) |  | P020PCB20CL010 | CCI-DAT-1461 | TBC | PRO-PID-44 | TAS3-108-01 | mm | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 21CP001 | Pump Station | TBC | Rosemount 2051CD3A02A1BS5M4Q4 | - |  |  |  | 0 | -2500 to 2500 | 0 to 250mbar | Pressure Differential Transmitter |  | P020GWA21CP001 | CCI-DAT-1460 | TBC | PRO-PID-42 | TAS3-207-01 | mbar(g) | mA | 0 | 62.5 | 125 | 187.5 | 250 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 200 |  | 50
Tauhara B Steamfield | Pump Station Seal Water System | 21CP002 | Pump Station | TBC | Rosemount 2051TG1A2B21BS5B4M4Q4Q8 | - |  |  |  | -0.34 | -1 to 2.1 | -0.7 to +0.7 | Pressure Indicating Transmitter |  | P020GWA21CP002 | CCI-DAT-1460 | TBC | PRO-PID-42 | TAS3-107-01 | bar(g) | mA | MVar1: -0.7; MVar2: -0.35; MVar3: 0; MVar4: 0.35; MVar5: 0.7; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 22CP010 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | - |  |  |  | 11.77 | -1 to 55 | 0 to 15 | Pressure Indicating Transmitter |  | P020GWA22CP010 | CCI-DAT-1460 | TBC | PRO-PID-42 | TAS3 106-01 | bar(g) | mA | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 22CP510 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA22CP510 | CCI-DAT-1460 | TBC | PRO-PID-42 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 30CF010 | Pump Station | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 8 | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWA30CF010 | CCI-DAT-1466 | TBC | PRO-PID-43 | TAS3-108-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 | 9.9 | 7 | 5
Tauhara B Steamfield | Pump Station Seal Water System | 30CF011 | Pump Station | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 8 | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWA30CF011 | CCI-DAT-1467 | TBC | PRO-PID-43 | TAS3-108-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 | 9.9 | 5 | 3
Tauhara B Steamfield | Pump Station Seal Water System | 31CF020 | Pump Station | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 8 | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWA31CF020 | CCI-DAT-1462 | TBC | PRO-PID-43 | TAS3-107-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 | 9.9 | 5 | 3
Tauhara B Steamfield | Pump Station Seal Water System | 30CF021 | Pump Station | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 8 | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWA31CF021 | CCI-DAT-1461 | TBC | PRO-PID-43 | TAS3-107-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 | 9.9 | 5 | 3
Tauhara B Steamfield | Pump Station Seal Water System | 32CF030 | Pump Station | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 8 | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWA32CF030 | CCI-DAT-1461 | TBC | PRO-PID-43 | TAS3-207-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 | 9.9 | 5 | 3
Tauhara B Steamfield | Pump Station Seal Water System | 32CF031 | Pump Station | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 8 | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWA32CF031 | CCI-DAT-1460 | TBC | PRO-PID-43 | TAS3-207-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 | 9.9 | 5 | 3
Tauhara B Steamfield | Pump Station Seal Water System | 33CF040 | Pump Station | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 8 | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWA33CF040 | CCI-DAT-1474 | TBC | PRO-PID-43 | TAS3-208-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 | 9.9 | 5 | 3
Tauhara B Steamfield | Pump Station Seal Water System | 33CF041 | Pump Station | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 8 | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWA33CF041 | CCI-DAT-1474 | TBC | PRO-PID-43 | Removed ILD by PL (rev. 3.6) | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 | 9.9 | 5 | 3
Tauhara B Steamfield | Pump Station Seal Water System | 30CP501 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA30CP501 | CCI-DAT-1474 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 30CP502 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA30CP502 | CCI-DAT-1474 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 30CP503 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA30CP503 | CCI-DAT-1474 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 30CT010 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 32 | 0 to 250 | 0 to 250 | Temperature Transmitter |  | P020GWA30CT010 | CCI-DAT-1474 | TBC | PRO-PID-43 | TAS3 104-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 50
Tauhara B Steamfield | Pump Station Seal Water System | 31CT020 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 32 | 0 to 250 | 0 to 250 | Temperature Transmitter |  | P020GWA31CT020 | CCI-DAT-1474 | TBC | PRO-PID-43 | TAS3 105-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 50
Tauhara B Steamfield | Pump Station Seal Water System | 32CT030 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 32 | 0 to 250 | 0 to 250 | Temperature Transmitter |  | P020GWA32CT030 | CCI-DAT-1474 | TBC | PRO-PID-43 | TAS3-205-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 50
Tauhara B Steamfield | Pump Station Seal Water System | 33CT040 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 32 | 0 to 250 | 0 to 250 | Temperature Transmitter |  | P020GWA33CT040 | CCI-DAT-1460 | TBC | PRO-PID-43 | TAS3-208-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 50
Tauhara B Steamfield | Pump Station Seal Water System | 31CP511 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA31CP511 | CCI-DAT-1460 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 31CP512 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA31CP512 | CCI-DAT-1460 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 31CP513 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA31CP513 | CCI-DAT-1465 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 32CP521 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA32CP521 | CCI-DAT-1465 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 32CP522 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA32CP522 | CCI-DAT-1465 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 32CP523 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA32CP523 | CCI-DAT-1465 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 33CP531 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA33CP531 | CCI-DAT-1460 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 33CP532 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA33CP532 | CCI-DAT-1460 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 33CP533 | Pump Station | TBC | Wika 72039876+14503369+ | - |  |  |  | 11.77 | 0 to 15 | - | Pressure Gauge |  | P020GWA33CP533 | CCI-DAT-1460 | TBC | PRO-PID-43 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 0; IdO2: 3.75; IdO3: 7.5; IdO4: 11.25; IdO5: 15
Tauhara B Steamfield | Pump Station Seal Water System | 10CL010 | Pump Station | TBC | Vega PS21.XXXXXGMHB+GFL-PULS.GG | - |  |  |  | N/A | 0 to 3000 | 0 to 3000 | Level Transmitter (Radar) |  | P020GWB10CL010 | CCI-DAT-1460 | TBC | PRO-PID-56 | TAS3-109-01 | mm | mA | MVar1: 0; MVar2: 750; MVar3: 1500; MVar4: 2250; MVar5: 3000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 10CL011 | Pump Station | TBC | Vendor Supplied | - |  |  |  | N/A | 0 to 3000 | 0 to 3000 | Level Indicator (Remote) |  | P020GWB10CL011 | CCI-DAT-1460 | TBC | PRO-PID-56 | vendor | mm | mm | MVar1: 0; MVar2: 750; MVar3: 1500; MVar4: 2250; MVar5: 3000; IdO1: 0; IdO2: 750; IdO3: 1500; IdO4: 2250; IdO5: 3000
Tauhara B Steamfield | Pump Station Seal Water System | 10CP510 | Pump Station | TBC | Rosemount 2051CD3A02A1BS5M4Q4+0305RC52B11B4 | - |  |  |  | 1.7 | 0 to 2.5 | 0 to 2.5 | Pressure Differential Transmitter |  | P020GWB10CP510 | CCI-DAT-1460 | TBC | PRO-PID-56 | TAS3-104-01 | bar(g) | mA | MVar1: 0; MVar2: 0.625; MVar3: 1.25; MVar4: 1.875; MVar5: 2.5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 21CF010 | Pump Station | TBC | SM6020, SMR12GGX50KG/US-100 | - |  |  |  | N/A | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWB21CF010 | CCI-DAT-1460 | TBC | PRO-PID-56 | TAS3-109-01 | l/m | mA | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 21CF020 | Pump Station | TBC | SM6020, SMR12GGX50KG/US-100 | - |  |  |  | N/A | 0 to 35 | 0 to 35 | Flow Transmitter (Magnetic) |  | P020GWB21CF020 | CCI-DAT-1460 | TBC | PRO-PID-56 | TAS3-109-01 | l/m | mA | MVar1: 0; MVar2: 8.75; MVar3: 17.5; MVar4: 26.25; MVar5: 35; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 21CP511 | Pump Station | TBC | Wika 72039878+14298395 | - |  |  |  | 13 | 0 to 25 | 0 to 25 | Pressure Gauge |  | P020GWB21CP511 | CCI-DAT-1460 | TBC | PRO-PID-56 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 0; IdO2: 6.25; IdO3: 12.5; IdO4: 18.75; IdO5: 25
Tauhara B Steamfield | Pump Station Seal Water System | 21CP521 | Pump Station | TBC | Wika 72039878+14298395 | - |  |  |  | 13 | 0 to 25 | 0 to 25 | Pressure Gauge |  | P020GWB21CP521 | CC-DAT-1468 | TBC | PRO-PID-56 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 0; IdO2: 6.25; IdO3: 12.5; IdO4: 18.75; IdO5: 25
Tauhara B Steamfield | Pump Station Seal Water System | 22CF010 | Pump Station | TBC | SM6020, SMR12GGX50KG/US-100 | - |  |  |  | N/A | 0 to 10 | 0 to 10 | Flow Transmitter (Magnetic) |  | P020GWB22CF010 |  | TBC | PRO-PID-56 | TAS3-109-01 | l/m | mA | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 22CF020 | Pump Station | TBC | SM6020, SMR12GGX50KG/US-100 | - |  |  |  | N/A | 0 to 35 | 0 to 35 | Flow Transmitter (Magnetic) |  | P020GWB22CF020 | CCI-DAT-1462 | TBC | PRO-PID-56 | TAS3-109-01 | l/m | mA | MVar1: 0; MVar2: 8.75; MVar3: 17.5; MVar4: 26.25; MVar5: 35; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Seal Water System | 22CP511 | Pump Station | TBC | Wika 72039878+14298395 | - |  |  |  | 13 | 0 to 25 | 0 to 25 | Pressure Gauge |  | P020GWB22CP511 | CCI-DAT-1474 | TBC | PRO-PID-56 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 0; IdO2: 6.25; IdO3: 12.5; IdO4: 18.75; IdO5: 25
Tauhara B Steamfield | Pump Station Seal Water System | 22CP521 | Pump Station | TBC | Wika 72039878+14298395 | - |  |  |  | 13 | 0 to 25 | 0 to 25 | Pressure Gauge |  | P020GWB22CP521 | CCI-DAT-1474 | TBC | PRO-PID-56 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 0; IdO2: 6.25; IdO3: 12.5; IdO4: 18.75; IdO5: 25
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CF010 | Pump Station | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 1120 | 0 to 1200 | 0 to 1200 | Flow Transmitter (Orifice Flow) |  | P020LFC20CF010 | CCI-DAT-1460 | TBC | PRO-PID-28 | TAS3-206-01 | tph | mA | MVar1: 0; MVar2: 300; MVar3: 600; MVar4: 900; MVar5: 1200; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL001 | Pump Station | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | N/A | 0 to 10000 | 0 to 10000 | Level Transmitter (Radar) |  | P020LFC20CL001 | CCI-DAT-1460 | TBC | PRO-PID-28 | TAS3 106-01 | mm | mA | MVar1: 0; MVar2: 2500; MVar3: 5000; MVar4: 7500; MVar5: 10000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL002 | Pump Station | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | N/A | 0 to 10000 | 0 to 10000 | Level Transmitter (Radar) |  | P020LFC20CL002 | CCI-DAT-1474 | TBC | PRO-PID-28 | TAS3-206-01 | mm | mA | MVar1: 0; MVar2: 2500; MVar3: 5000; MVar4: 7500; MVar5: 10000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL003 | Pump Station | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | N/A | 0 to 10000 | 0 to 10000 | Level Transmitter (Radar) |  | P020LFC20CL003 | CCI-DAT-1474 | TBC | PRO-PID-28 | TAS3-109-01 | mm | mA | MVar1: 0; MVar2: 2500; MVar3: 5000; MVar4: 7500; MVar5: 10000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL010 | Pump Station | TBC | Vega B86.IXCMAXAGDHXATMKM | - |  |  |  | 0 | 0 to 6000 | 0 to 6000 | Level Transmitter (Hydrostatic) |  | P020LFC20CL010 | CCI-DAT-1460 | TBC | PRO-PID-28 | TAS3-106-01 | mm | mA | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 200
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL020 | Pump Station | TBC | Vega B86.IXCMAXAGDHXATMKM | - |  |  |  | 0 | 0 to 6000 | 0 to 6000 | Level Transmitter (Hydrostatic) |  | P020LFC20CL020 | CCI-DAT-1460 | TBC | PRO-PID-28 | TAS3-107-01 | mm | mA | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 200
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL030 | Pump Station | TBC | Vega B86.IXCMAXAGDHXATMKM | - |  |  |  | 0 | 0 to 6000 | 0 to 6000 | Level Transmitter (Hydrostatic) |  | P020LFC20CL030 | CCI-DAT-1472 | TBC | PRO-PID-28 | TAS3-206-01 | mm | mA | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 200
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL040 | Pump Station | TBC | Vega B86.IXCMAXAGDHXATMKM | - |  |  |  | 0 | 0 to 6000 | 0 to 6000 | Level Transmitter (Hydrostatic) |  | P020LFC20CL040 | PRO-CAL-0039 | TBC | PRO-PID-28 | TAS3-207-01 | mm | mA | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 200
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CP010 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 16 | -1 to 55 | 0 to 25 | Pressure Indicating Transmitter |  | P020LFC20CP010 | CCI-DAT-1468 | TBC | PRO-PID-28 | TAS3 106-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 9
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT011 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 45 | 0 to 250 | 0 to 250 | Temperature Transmitter |  | P020LFC20CT011 | CCI-DAT-1468 | TBC | PRO-PID-28 | TAS3-201-01 | °C | mA | 0 | 62.5 | 125 | 187.5 | 250 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 43 | 45
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT012 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT012 | CCI-DAT-1468 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT013 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT013 | CCI-DAT-1480 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT014 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT014 | CCI-DAT-1480 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT015 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT015 | CCI-DAT-1480 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT016 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT016 | CCI-DAT-1480 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT022 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT022 | CCI-DAT-1461 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT023 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT023 | CCI-DAT-1465 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT024 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT024 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT025 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT025 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT026 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020LFC20CT026 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY010 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020LFC20CY010 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY011 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020LFC20CY011 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY012 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Speed Indicator |  | P020LFC20CY012 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY020 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020LFC20CY020 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY021 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020LFC20CY021 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY022 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Speed Indicator |  | P020LFC20CY022 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Condensate System | 10CF010 | Pump Station | TBC | Rosemount 8750WDMT2A2FNSA120CA1M4Q4Q8 | - |  |  |  | 455 | 0 to 10,000 | 0 to 600 | Flow Transmitter (Magnetic) |  | P020NAB10CF010 | PRO-DAT-0022 | TBC | PRO-PID-28 | TAS3 106-01 | tph | mA | MVar1: 0; MVar2: 150; MVar3: 300; MVar4: 450; MVar5: 600; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi4: 100
Tauhara B Steamfield | Pump Station Condensate System | 10CP010 | Pump Station | TBC | Rosemount 2051CD3A02A1BS5M4Q4 | - |  |  |  | 0 | -2500 to 2500 | 0 to 250mbar | Pressure Differential Transmitter |  | P020NAB10CP010 | PRO-DAT-0022 | TBC | PRO-PID-28 | TAS3 106-01 | mbar(g) | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 200
Tauhara B Steamfield | Pump Station Condensate System | 10CP011 | Pump Station | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 0.8 | -1 to 10.3 | 0 to 3 | Pressure Indicating Transmitter |  | P020NAB10CP011 | PRO-DAT-0022 | TBC | PRO-PID-28 | TAS3 106-01 | bar(g) | mA | MVar1: 0; MVar2: 0.75; MVar3: 1.5; MVar4: 2.25; MVar5: 3; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Condensate System | 10CP012 | Pump Station | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 3.5 | -1 to 10.3 | 0 to 10 | Pressure Indicating Transmitter |  | P020NAB10CP012 | PRO-DAT-0022 | TBC | PRO-PID-28 | TAS3 106-01 | bar(g) | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 |  | 6
Tauhara B Steamfield | Pump Station Condensate System | 10CP030 | Pump Station | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 3.5 | -1 to 10.3 | 0 to 10 | Pressure Indicating Transmitter |  | P020NAB10CP030 | PRO-DAT-0022 | TBC | PRO-PID-28 | TAS3-206-01 | bar(g) | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 9 |  | 1
Tauhara B Steamfield | Pump Station Condensate System | 10CT012 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NAB10CT012 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Condensate System | 10CT013 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NAB10CT013 | PRO-DAT-0022 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Condensate System | 10CT014 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NAB10CT014 | CCI-DAT-1474 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Condensate System | 10CT015 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NAB10CT015 | CCI-DAT-1462 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Condensate System | 10CT016 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NAB10CT016 | CCI-DAT-1461 | TBC | PRO-PID-28 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Condensate System | 10CT030 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 45 | 0 to 250 | 0 to 250 | Temperature Element |  | P020NAB10CT030 | CCI-DAT-1461 | TBC | PRO-PID-28 | TAS3 102-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 45
Tauhara B Steamfield | Pump Station Condensate System | 10CY010 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NAB10CY010 | CCI-DAT-1461 | TBC | PRO-PID-28 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Condensate System | 10CY011 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NAB10CY011 | PRO-DAT-0021 | TBC | PRO-PID-28 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Condensate System | 10CY012 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Speed Indicator |  | P020NAB10CY012 | PRO-DAT-0021 | TBC | PRO-PID-28 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CF010 | Pump Station | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 1067 | 0 to 1264 tph 0 to 622.7 mb | 0 to 1264 tph 0 to 622.7 mb | Flow Transmitter (Orifice Flow) |  | P020NDB10CF010 | PRO-DAT-0021 | TBC | PRO-PID-26 | TAS3-104-01 | tph | mA | MVar1: 0; MVar2: 316; MVar3: 632; MVar4: 948; MVar5: 1264; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CF020 | Pump Station | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 1067 | 0 to 1264 tph 0 to 622.7 mb | 0 to 1264 tph 0 to 622.7 mb | Flow Transmitter (Orifice Flow) |  | P020NDB10CF020 | PRO-DAT-0021 | TBC | PRO-PID-26 | TAS3-206-01 | tph | mA | 0 | 316 | 632 | 948 | 1264 |  |  | 4 | 8 | 12 | 16 | 20 |  |  |  |  | 40 | 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CF030 | Pump Station | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 1067 | 0 to 1264 tph 0 to 622.7 mb | 0 to 1264 tph 0 to 622.7 mb | Flow Transmitter (Orifice Flow) |  | P020NDB10CF030 | PRO-DAT-0021 | TBC | PRO-PID-26 | TAS3-205-01 | tph | mA | 0 | 316 | 632 | 948 | 1264 |  |  | 4 | 8 | 12 | 16 | 20 |  |  |  |  | 40 | 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CP011 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 35 | -1 to 55 | 0 to 45 | Pressure Indicating Transmitter |  | P020NDB10CP011 | CCI-DAT-1466 | TBC | PRO-PID-26 | TAS3 104-01 | bar(g) | mA | 0 | 11.25 | 22.5 | 33.75 | 45 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 10 |  | 0.5 | 0.3
Tauhara B Steamfield | Pump Station Separated Water System | 10CP014 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 35 | -1 to 55 | 0 to 45 | Pressure Indicating Transmitter |  | P020NDB10CP014 | PRO-DAT-0021 | TBC | PRO-PID-26 | TAS3-204-01 | bar(g) | mA | MVar1: 0; MVar2: 11.25; MVar3: 22.5; MVar4: 33.75; MVar5: 45; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CP015 | Pump Station | TBC | Wika 72039917 (Model 733.14.100)++11585791 (Model 910.15) | - |  |  |  | 0 | 0 to 500 | - | Pressure Differential Indicator |  | P020NDB10CP015 | PRO-DAT-0021 | TBC | PRO-PID-26 | 0 | mbar(g) | mbar | MVar1: 0; MVar2: 125; MVar3: 250; MVar4: 375; MVar5: 500; IdO1: 0; IdO2: 125; IdO3: 250; IdO4: 375; IdO5: 500
Tauhara B Steamfield | Pump Station Separated Water System | 10CP021 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 35 | -1 to 55 | 0 to 45 | Pressure Indicating Transmitter |  | P020NDB10CP021 | PRO-DAT-0021 | TBC | PRO-PID-26 | TAS3-105-01 | bar(g) | mA | MVar1: 0; MVar2: 11.25; MVar3: 22.5; MVar4: 33.75; MVar5: 45; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CP024 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 35 | -1 to 55 | 0 to 45 | Pressure Indicating Transmitter |  | P020NDB10CP024 | CCI-DAT-1472 | TBC | PRO-PID-26 | TAS3-206-01 | bar(g) | mA | MVar1: 0; MVar2: 11.25; MVar3: 22.5; MVar4: 33.75; MVar5: 45; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CP025 | Pump Station | TBC | Wika 72039917 (Model 733.14.100)++11585791 (Model 910.15) | - |  |  |  | 0 | 0 to 500 | - | Pressure Differential Indicator |  | P020NDB10CP025 | PRO-CAL-0039 | TBC | PRO-PID-26 | 0 | mbar(g) | mbar(g) | MVar1: 0; MVar2: 125; MVar3: 250; MVar4: 375; MVar5: 500; IdO1: 0; IdO2: 125; IdO3: 250; IdO4: 375; IdO5: 500
Tauhara B Steamfield | Pump Station Separated Water System | 10CP031 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 35 | -1 to 55 | 0 to 45 | Pressure Indicating Transmitter |  | P020NDB10CP031 | CCI-DAT-1472 | TBC | PRO-PID-26 | TAS3-109-01 | bar(g) | mA | 0 | 11.25 | 22.5 | 33.75 | 45 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 10 |  | 0.5 | 0.3
Tauhara B Steamfield | Pump Station Separated Water System | 10CP034 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 35 | -1 to 55 | 0 to 45 | Pressure Indicating Transmitter |  | P020NDB10CP034 | PRO-CAL-0039 | TBC | PRO-PID-26 | TAS3-205-01 | bar(g) | mA | MVar1: 0; MVar2: 11.25; MVar3: 22.5; MVar4: 33.75; MVar5: 45; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CP035 | Pump Station | TBC | Wika 72039917 (Model 733.14.100)++11585791 (Model 910.15) | - |  |  |  | 0 | 0 to 500 | - | Pressure Differential Indicator |  | P020NDB10CP035 | CCI-DAT-1472 | TBC | PRO-PID-26 | 0 | mbar(g) | mbar | MVar1: 0; MVar2: 125; MVar3: 250; MVar4: 375; MVar5: 500; IdO1: 0; IdO2: 125; IdO3: 250; IdO4: 375; IdO5: 500
Tauhara B Steamfield | Pump Station Separated Water System | 10CP040 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 35 | -1 to 55 | 0 to 45 | Pressure Indicating Transmitter |  | P020NDB10CP040 | PRO-CAL-0039 | TBC | PRO-PID-26 | TAS3-204-01 | bar(g) | mA | MVar1: 0; MVar2: 11.25; MVar3: 22.5; MVar4: 33.75; MVar5: 45; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CP512 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | 35 | See Notes | - | Pressure Gauge |  | P020NDB10CP512 | CCI-DAT-1461 | TBC | PRO-PID-26 | vendor | bar(g) | bar(g) | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Pump Station Separated Water System | 10CP513 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | 35 | See Notes | - | Pressure Gauge |  | P020NDB10CP513 | CCI-DAT-1461 | TBC | PRO-PID-26 | vendor | bar(g) | bar(g) | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Pump Station Separated Water System | 10CP522 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | 35 | See Notes | - | Pressure Gauge |  | P020NDB10CP522 | CCI-DAT-1462 | TBC | PRO-PID-26 | vendor | bar(g) | bar(g) | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Pump Station Separated Water System | 10CP523 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | 35 | See Notes | - | Pressure Gauge |  | P020NDB10CP523 | CCI-DAT-1461 | TBC | PRO-PID-26 | vendor | bar(g) | bar(g) | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Pump Station Separated Water System | 10CP532 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | 35 | See Notes | - | Pressure Gauge |  | P020NDB10CP532 | CCI-DAT-1461 | TBC | PRO-PID-26 | vendor | bar(g) | bar(g) | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Pump Station Separated Water System | 10CP533 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | 35 | See Notes | - | Pressure Gauge |  | P020NDB10CP533 | CCI-DAT-1462 | TBC | PRO-PID-26 | vendor | bar(g) | bar(g) | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Pump Station Separated Water System | 10CT010 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 123 | 0 to 250 | 0 to 250 | Temperature Element |  | P020NDB10CT010 | CCI-DAT-1461 | TBC | PRO-PID-26 | TAS3 101-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi3: 100
Tauhara B Steamfield | Pump Station Separated Water System | 10CT013 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT013 | CCI-DAT-1461 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT014 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT014 | CCI-DAT-1462 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT015 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT015 | CCI-DAT-1461 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT016 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT016 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT017 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT017 | 1460 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT020 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 123 | 0 to 250 | 0 to 250 | Temperature Element |  | P020NDB10CT020 | PRO-DAT-0020 | TBC | PRO-PID-26 | TAS3 103-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi3: 100
Tauhara B Steamfield | Pump Station Separated Water System | 10CT023 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT023 | 1460 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT024 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT024 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT025 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT025 | 1460 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT026 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT026 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT027 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT027 | 1460 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT030 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 120 | 0 to 250 | 0 to 250 | Temperature Element |  | P020NDB10CT030 | PRO-DAT-0020 | TBC | PRO-PID-26 | TAS3 102-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi3: 100
Tauhara B Steamfield | Pump Station Separated Water System | 10CT033 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT033 | 1460 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT034 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT034 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT035 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT035 | 1460 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT036 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT036 | CCI-DAT-1466 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CT037 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Temperature Element |  | P020NDB10CT037 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | °C | °C | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 0; IdO2: 0; IdO3: 0; IdO4: 0; IdO5: 0
Tauhara B Steamfield | Pump Station Separated Water System | 10CY010 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY010 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY011 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY011 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY012 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY012 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY013 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY013 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY014 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Speed Indicator |  | P020NDB10CY014 | CCI-DAT-1466 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY020 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY020 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY021 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY021 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY022 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY022 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY023 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY023 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY024 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Speed Indicator |  | P020NDB10CY024 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY030 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY030 | CCI-DAT-1466 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY031 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY031 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY032 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY032 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY033 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Vibration Transmitter |  | P020NDB10CY033 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Separated Water System | 10CY034 | Pump Station | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | Refer to Vendor | See Notes | - | Speed Indicator |  | P020NDB10CY034 | PRO-DAT-0020 | TBC | PRO-PID-26 | vendor | mm/s | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CF010 | Pump Station | TBC | Rosemount 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 707 | 0 to 720 | 0 to 720 | Flow Transmitter (Magnetic) |  | P020PCB20CF010 | PRO-DAT-0020 | TBC | PRO-PID-44 | TAS3-108-01 | l/m | mA | MVar1: 0; MVar2: 180; MVar3: 360; MVar4: 540; MVar5: 720; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi3: 500
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CF020 | Pump Station | TBC | Rosemount 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ | - |  |  |  | 707 | 0 to 720 | 0 to 720 | Flow Transmitter (Magnetic) |  | P020PCB20CF020 | PRO-DAT-0020 | TBC | PRO-PID-44 | TAS3-208-01 | l/m | mA | MVar1: 0; MVar2: 180; MVar3: 360; MVar4: 540; MVar5: 720; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi3: 500
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP010 | Pump Station | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 0.9 | -1 to 10.3 | 0 to 6 | Pressure Indicating Transmitter |  | P020PCB20CP010 | PRO-DAT-0020 | TBC | PRO-PID-44 | TAS3-108-01 | bar(g) | mA | MVar1: 0; MVar2: 1.5; MVar3: 3; MVar4: 4.5; MVar5: 6; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP040 | Pump Station | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 5.82 | -1 to 10.3 | 0 to 6 | Pressure Indicating Transmitter |  | P020PCB20CP040 | PRO-DAT-0020 | TBC | PRO-PID-44 | TAS3-208-01 | bar(g) | mA | 0 | 1.5 | 3 | 4.5 | 6 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 4.5 |  | 2 | 0.5
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP510 | Pump Station | TBC | Wika 72039938 (Model 433.50.100)+14503369 (IV10)+ | - |  |  |  | 0.9 | 0 to 10 | - | Pressure Gauge |  | P020PCB20CP510 | PRO-DAT-0020 | TBC | PRO-PID-44 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10; IdO1: 0; IdO2: 2.5; IdO3: 5; IdO4: 7.5; IdO5: 10
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP520 | Pump Station | TBC | Wika 72039938 (Model 433.50.100)+14503369 (IV10)+ | - |  |  |  | 5.82 | 0 to 10 | - | Pressure Gauge |  | P020PCB20CP520 | PRO-DAT-0020 | TBC | PRO-PID-44 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10; IdO1: 0; IdO2: 2.5; IdO3: 5; IdO4: 7.5; IdO5: 10
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP530 | Pump Station | TBC | Wika 72039938 (Model 433.50.100)+14503369 (IV10)+ | - |  |  |  | 5.82 | 0 to 10 | - | Pressure Gauge |  | P020PCB20CP530 | PRO-DAT-0020 | TBC | PRO-PID-44 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10; IdO1: 0; IdO2: 2.5; IdO3: 5; IdO4: 7.5; IdO5: 10
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CT010 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 30 | 0 to 250 | 0 to 250 | Temperature Element |  | P020PCB20CT010 | PRO-DAT-0020 | TBC | PRO-PID-46 | TAS3 101-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CT011 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 30 | 0 to 250 | 0 to 250 | Temperature Element |  | P020PCB20CT011 | PRO-DAT-0020 | TBC | PRO-PID-46 | TAS3-202-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CT012 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 30 | 0 to 250 | 0 to 250 | Temperature Element |  | P020PCB20CT012 | PRO-DAT-0020 | TBC | PRO-PID-46 | TAS3-203-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT011 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 40 | 0 to 250 | 0 to 250 | Temperature Element |  | P020PCB22CT011 | PRO-DAT-0020 | TBC | PRO-PID-45 | TAS3 103-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 35
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT012 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 40 | 0 to 250 | 0 to 250 | Temperature Element |  | P020PCB22CT012 | PRO-DAT-0020 | TBC | PRO-PID-45 | TAS3 103-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 35
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT013 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 40 | 0 to 250 | 0 to 250 | Temperature Element |  | P020PCB22CT013 | PRO-DAT-0020 | TBC | PRO-PID-45 | TAS3-202-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 35
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT021 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 30 | 0 to 250 | 0 to 250 | Temperature Element |  | P020PCB22CT021 | PRO-DAT-0020 | TBC | PRO-PID-45 | TAS3 104-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 35
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT022 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 30 | 0 to 250 | 0 to 250 | Temperature Element |  | P020PCB22CT022 | PRO-DAT-0020 | TBC | PRO-PID-45 | TAS3 104-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 35
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT023 | Pump Station | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 30 | 0 to 250 | 0 to 250 | Temperature Element |  | P020PCB22CT023 | PRO-DAT-0020 | TBC | PRO-PID-45 | TAS3-204-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 35
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT031 | Pump Station | TBC | Rosemount 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | - |  |  |  | 30 | 0 to 250 | - | Temperature Element |  | P020PCB22CT031 | CCI-DAT-1474 | TBC | PRO-PID-45 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 1; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT032 | Pump Station | TBC | Rosemount 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | - |  |  |  | 30 | 0 to 250 | - | Temperature Element |  | P020PCB22CT032 | CCI-DAT-1474 | TBC | PRO-PID-45 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 2; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT033 | Pump Station | TBC | Rosemount 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | - |  |  |  | 30 | 0 to 250 | - | Temperature Element |  | P020PCB22CT033 | CCI-DAT-1461 | TBC | PRO-PID-45 | 0 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 3; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP010 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 10 | -1 to 55 | 0 to 12 | Pressure Indicating Transmitter |  | P020QFB10CP010 | CCI-DAT-1461 | TBC | PRO-PID-47 | TAS3 108-01 | bar(g) | mA | MVar1: 0; MVar2: 3; MVar3: 6; MVar4: 9; MVar5: 12; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi3: 10
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP020 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 10 | -1 to 55 | 0 to 12 | Pressure Indicating Transmitter |  | P020QFB10CP020 | CCI-DAT-1460 | TBC | PRO-PID-47 | TAS3 109-01 | bar(g) | mA | MVar1: 0; MVar2: 3; MVar3: 6; MVar4: 9; MVar5: 12; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi3: 10
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP030 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 10 | -1 to 55 | 0 to 12 | Pressure Indicating Transmitter |  | P020QFB10CP030 | CCI-DAT-1460 | TBC | PRO-PID-47 | TAS2-206-01 | bar(g) | mA | MVar1: 0; MVar2: 3; MVar3: 6; MVar4: 9; MVar5: 12; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi3: 10
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP040 | Pump Station | TBC | Rosemount 3051TG3A2B21BB4M4T1Q4Q8S5 | - |  |  |  | 10 | -1 to 55 | 0 to 12 | Pressure Indicating Transmitter |  | P020QFB10CP040 | CCI-DAT-1460 | TBC | PRO-PID-47 | TAS2-206-01 | bar(g) | mA | MVar1: 0; MVar2: 3; MVar3: 6; MVar4: 9; MVar5: 12; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi3: 10
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP050 | Pump Station | TBC | Rosemount 3051TG3A2B21BB4M4T1Q4Q8S5 | - |  |  |  | 10 | -1 to 55 | 0 to 12 | Pressure Indicating Transmitter |  | P020QFB10CP050 | CCI-DAT-1466 | TBC | PRO-PID-47 | TAS2-206-01 | bar(g) | mA | MVar1: 0; MVar2: 3; MVar3: 6; MVar4: 9; MVar5: 12; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi3: 10
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP511 | Pump Station | TBC | Wika 72039879 + 14298395 | - |  |  |  | 10 | -1 to 55 | 0 to 16 | Pressure Gauge |  | P020QFB10CP511 | CCI-DAT-1466 | TBC | PRO-PID-47 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP521 | Pump Station | TBC | Wika 72039879 + 14298395 | - |  |  |  | 10 | -1 to 55 | 0 to 16 | Pressure Gauge |  | P020QFB10CP521 | CCI-DAT-1466 | TBC | PRO-PID-47 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP531 | Pump Station | TBC | Wika 72039879 + 14298395 | - |  |  |  | 10 | -1 to 55 | 0 to 16 | Pressure Gauge |  | P020QFB10CP531 | CCI-DAT-1466 | TBC | PRO-PID-47 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP541 | Pump Station | TBC | Wika 72039879 + 14298395 | - |  |  |  | 10 | -1 to 55 | 0 to 16 | Pressure Gauge |  | P020QFB10CP541 | CCI-DAT-1466 | TBC | PRO-PID-47 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP551 | Pump Station | TBC | Wika 72039879 + 14298395 | - |  |  |  | 10 | -1 to 55 | 0 to 16 | Pressure Gauge |  | P020QFB10CP551 | CCI-DAT-1466 | TBC | PRO-PID-47 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Pump Station Instrument Air System | 10CP523 | Pump Station | TBC | Wika 72039879 + 14298395 | - |  |  |  | 10 | -1 to 55 | 0 to 16 | Pressure Gauge |  | P020QFB10CP523 | CCI-DAT-1466 | TBC | PRO-PID-47 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Separation Plant Raw Water System | 10CL010 | Separation Plant | TBC | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - |  |  |  | N/A | See notes | TBC | Level Transmitter (Radar) |  | S020GAC10CL010 | CCI-DAT-1466 | TBC | PRO-PID-51 | TAS2-111-01 | mm | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Raw Water System | 10CL011 | Separation Plant | TBC | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - |  |  |  | N/A | See notes | TBC | Level Transmitter (Radar) |  | S020GAC10CL011 | CCI-DAT-1466 | TBC | PRO-PID-51 | TAS2-211-01 | mm | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Raw Water System | 10CL020 | Separation Plant | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | N/A | - | Refer to Notes | Level Gauge |  | S020GAC10CL020 | CCI-DAT-1466 | TBC | PRO-PID-51 | vendor | mm | mm | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Raw Water System | 10CL021 | Separation Plant | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | N/A | - | Refer to Notes | Level Gauge |  | S020GAC10CL021 | CCI-DAT-1466 | TBC | PRO-PID-51 | vendor | mm | mm | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Raw Water System | 10CP001 | Separation Plant | TBC | Rosemount 2051CD4A02A1BS5M4Q4 | - |  |  |  | 3.49 | 0 to 20 | 0 to 4 | Pressure Differential Transmitter |  | S020GAC10CP001 | CCI-DAT-1466 | TBC | PRO-PID-51 | TAS2-211-01 | bar(g) | mA | MVar1: 0; MVar2: 1; MVar3: 2; MVar4: 3; MVar5: 4; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 2
Tauhara B Steamfield | Separation Plant Raw Water System | 10CP002 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 2.98 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020GAC10CP002 | CCI-DAT-1461 | TBC | PRO-PID-51 | TAS2-211-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Raw Water System | 21CP020 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 2.98 | -1 to 10.3 | 0 to 8 | Pressure Indicating Transmitter |  | S020GAC21CP020 | CCI-DAT-1461 | TBC | PRO-PID-51 | TAS2-111-01 | bar(g) | mA | 0 | 2 | 4 | 6 | 8 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 4 |  | 1
Tauhara B Steamfield | Separation Plant Raw Water System | 22CF501 | Separation Plant | TBC | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - |  |  |  | Refer to Specification | Refer to Specification | - | Flow Indicator |  | S020GAC22CF501 | CCI-DAT-1461 | TBC | PRO-PID-101 | 0 | l/m | - | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Raw Water System | 22CF510 | Separation Plant | TBC | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - |  |  |  | Refer to Specification | Refer to Specification | - | Flow Indicator |  | S020GAC22CF510 | CCI-DAT-1461 | TBC | PRO-PID-101 | 0 | l/m | - | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Raw Water System | 22CF520 | Separation Plant | TBC | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - |  |  |  | Refer to Specification | Refer to Specification | - | Flow Indicator |  | S020GAC22CF520 | CCI-DAT-1461 | TBC | PRO-PID-100 | 0 | l/m | - | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Raw Water System | 22CF530 | Separation Plant | TBC | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - |  |  |  | Refer to Specification | Refer to Specification | - | Flow Indicator |  | S020GAC22CF530 | CCI-DAT-1460 | TBC | PRO-PID-100 | 0 | l/m | - | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Raw Water System | 22CF540 | Separation Plant | TBC | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - |  |  |  | Refer to Specification | Refer to Specification | - | Flow Indicator |  | S020GAC22CF540 | CCI-DAT-1460 | TBC | PRO-PID-100 | 0 | l/m | - | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Raw Water System | 22CF550 | Separation Plant | TBC | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - |  |  |  | Refer to Specification | Refer to Specification | - | Flow Indicator |  | S020GAC22CF550 | CCI-DAT-1460 | TBC | PRO-PID-100 | 0 | l/m | - | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Calcite Inhibitor Tank | 10CL010 | Separation Plant | TBC | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | - |  |  |  | N/A | 0 to 2500 | 0 to 2500 | Level Transmitter (Radar) |  | S020GBK10CL010 | CCI-DAT-1460 | TBC | PRO-PID-53 | TAS2-106-01 | mm | mA | MVar1: 0; MVar2: 625; MVar3: 1250; MVar4: 1875; MVar5: 2500; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Calcite Inhibitor Sump | 10CL011 | Separation Plant | TBC | Vega PS21.XXXXXGMHB+MBA.BB | - |  |  |  | N/A | 0 to 1000 | 0 to 1000 | Level Transmitter (Radar) |  | S020GBK10CL011 | CCI-DAT-1460 | TBC | PRO-PID-53 | TAS2-106-01 | mm | mA | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Calcite Inhibitor Tank | 10CL020 | Separation Plant | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | N/A | 0 to 2500 | 0 to 2500 | Level Gauge |  | S020GBK10CL020 | CCI-DAT-1460 | TBC | PRO-PID-53 | vendor | mm | mm | MVar1: 0; MVar2: 625; MVar3: 1250; MVar4: 1875; MVar5: 2500; IdO1: 0; IdO2: 625; IdO3: 1250; IdO4: 1875; IdO5: 2500
Tauhara B Steamfield | Separation Plant Calcite Inhibitor Tank | 10GS010 | Separation Plant | TBC | Schneider 56DOL9 Starter + TELE LRD12 Overload | - |  |  |  | N/A | - | - | Motor Starter (Local) |  | S020GBK10GS010 | CCI-DAT-1468 | TBC | PRO-PID-53 | 0 | - | - | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Potable Water System | 10CL010 | Separation Plant | TBC | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - |  |  |  | N/A | See notes | TBC | Level Transmitter (Radar) |  | S020GKA10CL010 | CCI-DAT-1468 | TBC | PRO-PID-40 | TAS2-111-01 | mm | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Potable Water System | 10CL011 | Separation Plant | TBC | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - |  |  |  | N/A | See notes | TBC | Level Transmitter (Radar) |  | S020GKA10CL011 | CCI-DAT-1471 | TBC | PRO-PID-40 | TAS2-211-01 | mm | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Potable Water System | 10CL020 | Separation Plant | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | N/A | - | Refer to Notes | Level Gauge |  | S020GKA10CL020 | PRO-DAT-0088 | TBC | PRO-PID-40 | vendor | mm | mm | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Potable Water System | 10CL021 | Separation Plant | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | N/A | - | Refer to Notes | Level Gauge |  | S020GKA10CL021 | CCI-DAT-1471 | TBC | PRO-PID-40 | vendor | mm | mm | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Potable Water System | 21CF191 | Separation Plant | TBC | Wika 72039911++ (FSD-4 Model) | - |  |  |  | >1.5 | 0 to 2 | N/A | Flow Switch |  | S020GKA21CF191 | PRO-DAT-0088 | TBC | PRO-PID-40 | TAS2-606-02 | kg/s | kg/s | MVar1: 0; MVar2: 0.5; MVar3: 1; MVar4: 1.5; MVar5: 2; IdO1: 0; IdO2: 0.5; IdO3: 1; IdO4: 1.5; IdO5: 2
Tauhara B Steamfield | Separation Plant Potable Water System | 21CF192 | Separation Plant | TBC | Wika 72039911++ (FSD-4 Model) | - |  |  |  | >1.5 | 0 to 2 | N/A | Flow Switch |  | S020GKA21CF192 | CCI-DAT-1462 | TBC | PRO-PID-40 | TAS2-606-02 | kg/s | kg/s | MVar1: 0; MVar2: 0.5; MVar3: 1; MVar4: 1.5; MVar5: 2; IdO1: 0; IdO2: 0.5; IdO3: 1; IdO4: 1.5; IdO5: 2
Tauhara B Steamfield | Separation Plant Potable Water System | 21CF193 | Separation Plant | TBC | Wika 72039911++ (FSD-4 Model) | - |  |  |  | >1.5 | 0 to 2 | N/A | Flow Switch |  | S020GKA21CF193 | CCI-DAT-1461 | TBC | PRO-PID-40 | TAS2-606-02 | kg/s | kg/s | MVar1: 0; MVar2: 0.5; MVar3: 1; MVar4: 1.5; MVar5: 2; IdO1: 0; IdO2: 0.5; IdO3: 1; IdO4: 1.5; IdO5: 2
Tauhara B Steamfield | Separation Plant Potable Water System | 21CF194 | Separation Plant | TBC | Wika 72039911++ (FSD-4 Model) | - |  |  |  | >1.5 | 0 to 4 | N/A | Flow Switch |  | S020GKA21CF194 | CCI-DAT-1461 | TBC | PRO-PID-40 | TAS2-212-01 | kg/s | kg/s | MVar1: 0; MVar2: 1; MVar3: 2; MVar4: 3; MVar5: 4; IdO1: 0; IdO2: 1; IdO3: 2; IdO4: 3; IdO5: 4
Tauhara B Steamfield | Pump Station Potable Water System | 21CF195 | Pump Station | TBC | Wika 72039911++ (FSD-4 Model) | - |  |  |  | >1.5 | 0 to 3 | N/A | Flow Switch |  | S020GKA21CF195 | QCM-PRO-SPC-0109 | TBC | PRO-PID-40 | 0 | kg/s | kg/s | MVar1: 0; MVar2: 0.75; MVar3: 1.5; MVar4: 2.25; MVar5: 3; IdO1: 0; IdO2: 0.75; IdO3: 1.5; IdO4: 2.25; IdO5: 3
Tauhara B Steamfield | Pump Station Potable Water System | 21CF196 | Pump Station | TBC | Wika 72039911++ (FSD-4 Model) | - |  |  |  | >1.5 | 0 to 3 | N/A | Flow Switch |  | S020GKA21CF196 | QCM-PRO-SPC-0109 | TBC | PRO-PID-40 | 0 | kg/s | kg/s | MVar1: 0; MVar2: 0.75; MVar3: 1.5; MVar4: 2.25; MVar5: 3; IdO1: 0; IdO2: 0.75; IdO3: 1.5; IdO4: 2.25; IdO5: 3
Tauhara B Steamfield | Separation Plant Potable Water System | 20CP520 | Separation Plant | TBC | Wika 72039882 (Model 433.50)+14503369+ (Model IV10) | - |  |  |  | 3.14 | 0 to 25 | - | Pressure Gauge |  | S020GKA20CP520 | QCM-PRO-SPC-0109 | TBC | PRO-PID-40 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 0; IdO2: 6.25; IdO3: 12.5; IdO4: 18.75; IdO5: 25
Tauhara B Steamfield | Separation Plant Acid Dosing System | 11CF010 | Separation Plant | TBC | Vendor Supplied | - |  |  |  | - | - | 0 | Flow Transmitter (Magnetic) |  | S020GWA11CF010 | QCM-PRO-SPC-0109 | TBC | PRO-PID-55 | 0 | 0 | mA | MVar1: -; MVar2: -; MVar3: -; MVar4: -; MVar5: -; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 11CF020 | Separation Plant | TBC | Vendor Supplied | - |  |  |  | - | - | 0 | Flow Transmitter (Magnetic) |  | S020GWA11CF020 | QCM-PRO-SPC-0109 | TBC | PRO-PID-55 | 0 | 0 | mA | MVar1: -; MVar2: -; MVar3: -; MVar4: -; MVar5: -; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CL310 | Separation Plant | TBC | Vega P21.XXXXXABMIB | - |  |  |  | - | - | 0 | Level Switch |  | S020GWA10CL310 | QCM-PRO-SPC-0109 | TBC | PRO-PID-55 | 0 | mm | mm | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | Separation Plant Acid Dosing System | 12CT010 | Separation Plant | TBC | Rosemount 644HANAJ5M5Q4+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAA2SC075AQ35Q5Q8XW | - |  |  |  | 123 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | S020GWA12CT010 | CCI-DAT-1468 | TBC | PRO-PID-55 | 0 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT010 | Separation Plant | TBC | Servotech QT21GS2+QR08N+HKNPB | - |  |  |  | 123 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | S020GWA10CT010 |  | TBC | PRO-PID-55 | 0 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT020 | Separation Plant | TBC | Servotech QT21GS2+QR08N+HKNPB | - |  |  |  | 123 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | S020GWA10CT020 | CCI-DAT-1468 | TBC | PRO-PID-55 | 0 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 11CP510 | Separation Plant | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | - | See notes | 0 | Pressure Differential Transmitter |  | S020GWA11CP510 | CCI-DAT-1468 | TBC | PRO-PID-55 | 0 | - | mA | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | Separation Plant Process Water System | 10CF010 | Separation Plant | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 7.6 | 0 to 18 | 0 to 18 | Flow Transmitter (Orifice Flow) |  | S020LCE10CF010 | CCI-DAT-1471 | TBC | PRO-PID-18 | TAS2-109-01 | tph | mA | 0 | 4.5 | 9 | 13.5 | 18 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 250 |  | 50
Tauhara B Steamfield | Separation Plant Process Water System | 10CF020 | Separation Plant | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 2.2 | 0 to 7.2 | 0 to 7.2 | Flow Transmitter (Orifice Flow) |  | S020LCE10CF020 | PRO-DAT-0074 | TBC | PRO-PID-20 | TAS2-209-01 | tph | mA | 0 | 1.8 | 3.6 | 5.4 | 7.2 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 100 |  | 20 | L/min
Tauhara B Steamfield | Separation Plant Process Water System | 10CF030 | Separation Plant | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 1.8 | 0 to 7.2 | 0 to 7.2 | Flow Transmitter (Orifice Flow) |  | S020LCE10CF030 | CCI-DAT-1471 | TBC | PRO-PID-22 | TAS2-109-01 | tph | mA | 0 | 1.8 | 3.6 | 5.4 | 7.2 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 100 |  | 20 | L/min
Tauhara B Steamfield | Separation Plant Process Water System | 10CF040 | Separation Plant | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 1.8 | 0 to 7.2 | 0 to 7.2 | Flow Transmitter (Orifice Flow) |  | S020LCE10CF040 | PRO-DAT-0074 | TBC | PRO-PID-24 | TAS2-209-01 | tph | mA | 0 | 1.8 | 3.6 | 5.4 | 7.2 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 100 |  | 20 | L/min
Tauhara B Steamfield | Separation Plant Process Water System | 10CP510 | Separation Plant | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 16.72 | 0 to 60 | - | Pressure Gauge |  | S020LCE10CP510 | CCI-DAT-1476 | TBC | PRO-PID-18 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Separation Plant Process Water System | 10CP520 | Separation Plant | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 8.78 | 0 to 60 | - | Pressure Gauge |  | S020LCE10CP520 | CCI-DAT-1476 | TBC | PRO-PID-20 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Separation Plant Process Water System | 10CP530 | Separation Plant | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 1.16 | 0 to 60 | - | Pressure Gauge |  | S020LCE10CP530 | CCI-DAT-1476 | TBC | PRO-PID-22 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Separation Plant Process Water System | 10CP540 | Separation Plant | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 1.16 | 0 to 60 | - | Pressure Gauge |  | S020LCE10CP540 | CCI-DAT-1476 | TBC | PRO-PID-24 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Separation Plant Deoxygenated Tank 1 | 20CL010 | Separation Plant | TBC | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | - |  |  |  | N/A | 0 to 3125 | 0 to 3125 | Level Transmitter (Radar) |  | S020LCE20CL010 | CCI-DAT-1476 | TBC | PRO-PID-53 | TAS2-106-01 | mm | mA | MVar1: 0; MVar2: 781.25; MVar3: 1562.5; MVar4: 2343.75; MVar5: 3125; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Deoxygenated Tank 2 | 20CL011 | Separation Plant | TBC | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | - |  |  |  | N/A | 0 to 3125 | 0 to 3125 | Level Transmitter (Radar) |  | S020LCE20CL011 | CCI-DAT-1476 | TBC | PRO-PID-53 | TAS2-206-01 | mm | mA | MVar1: 0; MVar2: 781.25; MVar3: 1562.5; MVar4: 2343.75; MVar5: 3125; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Deoxygenated Tank 1 | 20CL020 | Separation Plant | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | N/A | 0 to 3125 | 0 to 3125 | Level Gauge |  | S020LCE20CL020 | CCI-DAT-1460 | TBC | PRO-PID-53 | vendor | mm | mm | MVar1: 0; MVar2: 781.25; MVar3: 1562.5; MVar4: 2343.75; MVar5: 3125; IdO1: 0; IdO2: 781.25; IdO3: 1562.5; IdO4: 2343.75; IdO5: 3125
Tauhara B Steamfield | Separation Plant Deoxygenated Tank 2 | 20CL021 | Separation Plant | TBC | Vendor Supplied Vendor Supplied | - |  |  |  | N/A | 0 to 3125 | 0 to 3125 | Level Gauge |  | S020LCE20CL021 |  | TBC | PRO-PID-53 | vendor | mm | mm | MVar1: 0; MVar2: 781.25; MVar3: 1562.5; MVar4: 2343.75; MVar5: 3125; IdO1: 0; IdO2: 781.25; IdO3: 1562.5; IdO4: 2343.75; IdO5: 3125
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT001 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 226.1 | 0 to 250 | 0 to 250 | Temperature Element |  | L050NDA10CT001 |  | TBC | PRO-PID-11 | TAS2-201-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT002 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 226.1 | 0 to 250 | 0 to 250 | Temperature Element |  | L050NDA10CT002 |  | TBC | PRO-PID-11 | TAS2-203-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT003 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 226.1 | 0 to 250 | 0 to 250 | Temperature Element |  | L050NDA10CT003 | CCI-DAT-1465 | TBC | PRO-PID-11 | TAS2-204-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT011 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 226.1 | 0 to 250 | 0 to 250 | Temperature Element |  | L060NDA10CT011 | CCI-DAT-1465 | TBC | PRO-PID-11 | TAS2-101-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT012 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 226.1 | 0 to 250 | 0 to 250 | Temperature Element |  | L060NDA10CT012 | CCI-DAT-1465 | TBC | PRO-PID-11 | TAS2-103-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT013 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 226.1 | 0 to 250 | 0 to 250 | Temperature Element |  | L060NDA10CT013 | CCI-DAT-1465 | TBC | PRO-PID-11 | TAS2-104-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT021 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 226.1 | 0 to 250 | 0 to 250 | Temperature Element |  | L070NDA10CT021 | CCI-DAT-1465 | TBC | PRO-PID-11 | TAS2-101-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT022 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 226.1 | 0 to 250 | 0 to 250 | Temperature Element |  | L070NDA10CT022 |  | TBC | PRO-PID-11 | TAS2-103-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT023 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 226.1 | 0 to 250 | 0 to 250 | Temperature Element |  | L070NDA10CT023 | CCI-DAT-1472 | TBC | PRO-PID-11 | TAS2-104-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT041 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 215 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA10CT041 | PRO-CAL-0039 | TBC | PRO-PID-18 | TAS2-101-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT042 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 215 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA10CT042 | CCI-DAT-1472 | TBC | PRO-PID-18 | TAS2-102-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT043 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 215 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA10CT043 | PRO-CAL-0039 | TBC | PRO-PID-18 | TAS2-103-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT044 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 215 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA10CT044 | CCI-DAT-1472 | TBC | PRO-PID-18 | TAS2-201-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT045 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 215 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA10CT045 | PRO-CAL-0039 | TBC | PRO-PID-18 | TAS2-202-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT046 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 215 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA10CT046 | CCI-DAT-1472 | TBC | PRO-PID-18 | TAS2-203-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT051 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 188 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA20CT051 | PRO-CAL-0039 | TBC | PRO-PID-20 | TAS2-101-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT052 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 188 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA20CT052 | CCI-DAT-1460 | TBC | PRO-PID-20 | TAS2-102-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT053 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 188 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA20CT053 | CCI-DAT-1460 | TBC | PRO-PID-20 | TAS2-103-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT054 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 188 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA20CT054 | CCI-DAT-1460 | TBC | PRO-PID-20 | TAS2-201-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT061 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA31CT061 | CCI-DAT-1460 | TBC | PRO-PID-22 | TAS2-101-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT062 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA31CT062 | CCI-DAT-1468 | TBC | PRO-PID-22 | TAS2-102-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT063 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA31CT063 | CCI-DAT-1468 | TBC | PRO-PID-22 | TAS2-103-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT064 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA31CT064 | CCI-DAT-1471 | TBC | PRO-PID-22 | TAS2-201-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT065 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA31CT065 | CCI-DAT-1471 | TBC | PRO-PID-22 | TAS2-202-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT066 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA31CT066 | CCI-DAT-1466 | TBC | PRO-PID-22 | TAS2-203-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT071 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA32CT071 | CCI-DAT-1466 | TBC | PRO-PID-24 | TAS2-101-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT072 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA32CT072 | CCI-DAT-1466 | TBC | PRO-PID-24 | TAS2-102-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT073 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA32CT073 | CCI-DAT-1466 | TBC | PRO-PID-24 | TAS2-103-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT074 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA32CT074 | CCI-DAT-1466 | TBC | PRO-PID-24 | TAS2-201-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT075 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA32CT075 | CCI-DAT-1466 | TBC | PRO-PID-24 | TAS2-202-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT076 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 143 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NAA32CT076 | CCI-DAT-1466 | TBC | PRO-PID-24 | TAS2-203-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 100
Tauhara B Steamfield | Separation Plant Steam System | 10CF010 | Separation Plant | TBC | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - |  |  |  | 740 | 0 to 900 | 0 to 900 | Flow Transmitter (Vortex) |  | S020NAA10CF010 | CCI-DAT-1466 | TBC | PRO-PID-18 | TAS2-209-01 | tph | mA | MVar1: 0; MVar2: 225; MVar3: 450; MVar4: 675; MVar5: 900; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 10CL410 | Separation Plant | TBC | Bliss Anand R/36/M/S/2/1/B/N/N/X/PN/S/772MM | - |  |  |  | - | - | 0 to 800 | Level Gauge |  | S020NAA10CL410 | CCI-DAT-1466 | TBC | PRO-PID-18 | 0 | mm | mm | MVar1: 0; MVar2: 200; MVar3: 400; MVar4: 600; MVar5: 800; IdO1: 0; IdO2: 200; IdO3: 400; IdO4: 600; IdO5: 800
Tauhara B Steamfield | Separation Plant Steam System | 10CL450 | Separation Plant | TBC | Bliss Anand R/47/M/S/2/1/B/N/N/X/PN/S/1156MM | - |  |  |  | N/A | - | 0 to 1200 | Level Gauge |  | S020NAA10CL450 | CCI-DAT-1466 | TBC | PRO-PID-19 | 0 | mm | mm | MVar1: 0; MVar2: 300; MVar3: 600; MVar4: 900; MVar5: 1200; IdO1: 0; IdO2: 300; IdO3: 600; IdO4: 900; IdO5: 1200
Tauhara B Steamfield | Separation Plant Steam System | 10CL451 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00120ABNAM1Q4Q8QTDA1S2 | - |  |  |  | N/A | 0 to 1200 | 0 to 1200 | Level Transmitter (GW Radar) |  | S020NAA10CL451 | CCI-DAT-1466 | TBC | PRO-PID-19 | TAS2-109-01 | mm | mA | 0 | 300 | 600 | 900 | 1200 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 1100 |  | 100
Tauhara B Steamfield | Separation Plant Steam System | 10CL460 | Separation Plant | TBC | Bliss Anand R/36/M/S/2/1/B/N/N/X/PN/S/772MM | - |  |  |  | N/A | - | 0 to 800 | Level Gauge |  | S020NAA10CL460 | CCI-DAT-1466 | TBC | PRO-PID-19 | 0 | mm | mm | MVar1: 0; MVar2: 200; MVar3: 400; MVar4: 600; MVar5: 800; IdO1: 0; IdO2: 200; IdO3: 400; IdO4: 600; IdO5: 800
Tauhara B Steamfield | Separation Plant Steam System | 10CP021 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 17 | -1 to 55 | 0 to 23 | Pressure Indicating Transmitter |  | S020NAA10CP021 | CCI-DAT-1466 | TBC | PRO-PID-12 | TAS2-106-01 | bar(g) | mA | MVar1: 0; MVar2: 5.75; MVar3: 11.5; MVar4: 17.25; MVar5: 23; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 10CP022 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 17 | -1 to 55 | 0 to 23 | Pressure Indicating Transmitter |  | S020NAA10CP022 | CCI-DAT-1466 | TBC | PRO-PID-12 | TAS2-107-01 | bar(g) | mA | MVar1: 0; MVar2: 5.75; MVar3: 11.5; MVar4: 17.25; MVar5: 23; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 10CP023 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 17 | -1 to 55 | 0 to 23 | Pressure Indicating Transmitter |  | S020NAA10CP023 | CCI-DAT-1466 | TBC | PRO-PID-12 | TAS2-206-01 | bar(g) | mA | MVar1: 0; MVar2: 5.75; MVar3: 11.5; MVar4: 17.25; MVar5: 23; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 10CP031 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - |  |  |  | 17 | -1 to 55 | 0 to 23 | Pressure Indicating Transmitter |  | S020NAA10CP031 | CCI-DAT-1466 | TBC | PRO-PID-12 | TAS4-101-01 | bar(g) | mA | MVar1: 0; MVar2: 5.75; MVar3: 11.5; MVar4: 17.25; MVar5: 23; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 10CP032 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - |  |  |  | 17 | -1 to 55 | 0 to 23 | Pressure Indicating Transmitter |  | S020NAA10CP032 | CCI-DAT-1466 | TBC | PRO-PID-12 | TAS4-102-01 | bar(g) | mA | MVar1: 0; MVar2: 5.75; MVar3: 11.5; MVar4: 17.25; MVar5: 23; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 10CP033 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - |  |  |  | 17 | -1 to 55 | 0 to 23 | Pressure Indicating Transmitter |  | S020NAA10CP033 | CCI-DAT-1466 | TBC | PRO-PID-12 | TAS4-103-01 | bar(g) | mA | MVar1: 0; MVar2: 5.75; MVar3: 11.5; MVar4: 17.25; MVar5: 23; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 11CF452 | Separation Plant | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 8.7 | 0 to 20 | 0 to 18 | Flow Transmitter (Orifice Flow) |  | S020NAA11CF452 | CCI-DAT-1466 | TBC | PRO-PID-19 | TAS2-109-01 | tph | mA | 0 | 4.5 | 9 | 13.5 | 18 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 250 |  | 20
Tauhara B Steamfield | Separation Plant Steam System | 20CF010 | Separation Plant | TBC | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - |  |  |  | 191 | 0 to 216 | 0 to 216 | Flow Transmitter (Vortex) |  | S020NAA20CF010 | CCI-DAT-1466 | TBC | PRO-PID-21 | TAS2-209-01 | tph | mA | MVar1: 0; MVar2: 54; MVar3: 108; MVar4: 162; MVar5: 216; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 20CL410 | Separation Plant | TBC | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM | - |  |  |  | N/A | - | 0 to 600 | Level Gauge |  | S020NAA20CL410 | CCI-DAT-1466 | TBC | PRO-PID-20 | 0 | mm | mm | MVar1: 0; MVar2: 150; MVar3: 300; MVar4: 450; MVar5: 600; IdO1: 0; IdO2: 150; IdO3: 300; IdO4: 450; IdO5: 600
Tauhara B Steamfield | Separation Plant Steam System | 20CL450 | Separation Plant | TBC | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM | - |  |  |  | N/A | - | 0 to 600 | Level Gauge |  | S020NAA20CL450 | CCI-DAT-1466 | TBC | PRO-PID-21 | 0 | mm | mm | MVar1: 0; MVar2: 150; MVar3: 300; MVar4: 450; MVar5: 600; IdO1: 0; IdO2: 150; IdO3: 300; IdO4: 450; IdO5: 600
Tauhara B Steamfield | Separation Plant Steam System | 20CL460 | Separation Plant | TBC | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM | - |  |  |  | N/A | - | 0 to 600 | Level Gauge |  | S020NAA20CL460 | CCI-DAT-1466 | TBC | PRO-PID-21 | 0 | mm | mm | MVar1: 0; MVar2: 150; MVar3: 300; MVar4: 450; MVar5: 600; IdO1: 0; IdO2: 150; IdO3: 300; IdO4: 450; IdO5: 600
Tauhara B Steamfield | Separation Plant Steam System | 20CP021 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 9 | -1 to 55 | 0 to 15 | Pressure Indicating Transmitter |  | S020NAA20CP021 | CCI-DAT-1466 | TBC | PRO-PID-20 | TAS2-106-01 | bar(g) | mA | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 20CP022 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 9 | -1 to 55 | 0 to 15 | Pressure Indicating Transmitter |  | S020NAA20CP022 | CCI-DAT-1466 | TBC | PRO-PID-20 | TAS2-107-01 | bar(g) | mA | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 20CP023 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 9 | -1 to 55 | 0 to 15 | Pressure Indicating Transmitter |  | S020NAA20CP023 | CCI-DAT-1466 | TBC | PRO-PID-20 | TAS2-207-01 | bar(g) | mA | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 20CP031 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - |  |  |  | 9 | -1 to 55 | 0 to 13 | Pressure Indicating Transmitter |  | S020NAA20CP031 | CCI-DAT-1466 | TBC | PRO-PID-20 | TAS4-101-01 | bar(g) | mA | MVar1: 0; MVar2: 3.25; MVar3: 6.5; MVar4: 9.75; MVar5: 13; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 20CP032 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - |  |  |  | 9 | -1 to 55 | 0 to 13 | Pressure Indicating Transmitter |  | S020NAA20CP032 | CCI-DAT-1466 | TBC | PRO-PID-20 | TAS4-102-01 | bar(g) | mA | MVar1: 0; MVar2: 3.25; MVar3: 6.5; MVar4: 9.75; MVar5: 13; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 20CP033 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - |  |  |  | 9 | -1 to 55 | 0 to 13 | Pressure Indicating Transmitter |  | S020NAA20CP033 | CCI-DAT-1466 | TBC | PRO-PID-20 | TAS4-103-01 | bar(g) | mA | MVar1: 0; MVar2: 3.25; MVar3: 6.5; MVar4: 9.75; MVar5: 13; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 31CF010 | Separation Plant | TBC | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - |  |  |  | 162 | 0 to 216 | 0 to 216 | Flow Transmitter (Vortex) |  | S020NAA31CF010 | CCI-DAT-1466 | TBC | PRO-PID-22 | TAS2-109-01 | tph | mA | MVar1: 0; MVar2: 54; MVar3: 108; MVar4: 162; MVar5: 216; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 31CL410 | Separation Plant | TBC | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - |  |  |  | N/A | - | 0 to 1000 | Level Gauge |  | S020NAA31CL410 | CCI-DAT-1466 | TBC | PRO-PID-22 | 0 | mm | mm | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000; IdO1: 0; IdO2: 250; IdO3: 500; IdO4: 750; IdO5: 1000
Tauhara B Steamfield | Separation Plant Steam System | 31CL450 | Separation Plant | TBC | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - |  |  |  | N/A | - | 0 to 1000 | Level Gauge |  | S020NAA31CL450 | CCI-DAT-1478 | TBC | PRO-PID-23 | 0 | mm | mm | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000; IdO1: 0; IdO2: 250; IdO3: 500; IdO4: 750; IdO5: 1000
Tauhara B Steamfield | Separation Plant Steam System | 31CL460 | Separation Plant | TBC | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - |  |  |  | N/A | - | 0 to 1000 | Level Gauge |  | S020NAA31CL460 | CCI-DAT-1471 | TBC | PRO-PID-23 | 0 | mm | mm | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000; IdO1: 0; IdO2: 250; IdO3: 500; IdO4: 750; IdO5: 1000
Tauhara B Steamfield | Separation Plant Steam System | 31CP021 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA31CP021 | CCI-DAT-1471 | TBC | PRO-PID-14 | TAS2-108-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 31CP022 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA31CP022 | CCI-DAT-1469 | TBC | PRO-PID-14 | TAS2-109-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 31CP023 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA31CP023 | CCI-DAT-1471 | TBC | PRO-PID-14 | TAS2-208-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 31CP031 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA31CP031 | CCI-DAT-1461 | TBC | PRO-PID-14 | TAS4-101-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 31CP032 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA31CP032 | CCI-DAT-1461 | TBC | PRO-PID-14 | TAS4-102-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 31CP033 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA31CP033 | CCI-DAT-1461 | TBC | PRO-PID-14 | TAS4-103-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 32CF010 | Separation Plant | TBC | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - |  |  |  | 162 | 0 to 216 | 0 to 216 | Flow Transmitter (Vortex) |  | S020NAA32CF010 | CCI-DAT-1461 | TBC | PRO-PID-24 | TAS2-209-01 | tph | mA | MVar1: 0; MVar2: 54; MVar3: 108; MVar4: 162; MVar5: 216; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 32CL410 | Separation Plant | TBC | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - |  |  |  | N/A | - | 0 to 1000 | Level Gauge |  | S020NAA32CL410 | CCI-DAT-1461 | TBC | PRO-PID-24 | 0 | mm | mm | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000; IdO1: 0; IdO2: 250; IdO3: 500; IdO4: 750; IdO5: 1000
Tauhara B Steamfield | Separation Plant Steam System | 32CL450 | Separation Plant | TBC | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - |  |  |  | N/A | - | 0 to 1000 | Level Gauge |  | S020NAA32CL450 | CCI-DAT-1461 | TBC | PRO-PID-25 | 0 | mm | mm | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000; IdO1: 0; IdO2: 250; IdO3: 500; IdO4: 750; IdO5: 1000
Tauhara B Steamfield | Separation Plant Steam System | 32CL460 | Separation Plant | TBC | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - |  |  |  | N/A | - | 0 to 1000 | Level Gauge |  | S020NAA32CL460 | CCI-DAT-1472 | TBC | PRO-PID-25 | 0 | mm | mm | MVar1: 0; MVar2: 250; MVar3: 500; MVar4: 750; MVar5: 1000; IdO1: 0; IdO2: 250; IdO3: 500; IdO4: 750; IdO5: 1000
Tauhara B Steamfield | Separation Plant Steam System | 32CP021 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA32CP021 | PRO-CAL-0039 | TBC | PRO-PID-14 | TAS2-208-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 32CP022 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA32CP022 | CCI-DAT-1478 | TBC | PRO-PID-14 | TAS2-209-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 32CP023 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA32CP023 | CCI-DAT-1471 | TBC | PRO-PID-14 | TAS2-108-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 32CP031 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA32CP031 | CCI-DAT-1471 | TBC | PRO-PID-14 | TAS4-101-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 32CP032 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA32CP032 | CCI-DAT-1471 | TBC | PRO-PID-14 | TAS4-102-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Steam System | 32CP033 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NAA32CP033 | CCI-DAT-1461 | TBC | PRO-PID-14 | TAS4-103-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CL011 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (GW Radar) |  | S020NDA10CL011 | CCI-DAT-1461 | TBC | PRO-PID-12 | TAS4-101-01 | mm | mA | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CL012 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (GW Radar) |  | S020NDA10CL012 | CCI-DAT-1461 | TBC | PRO-PID-12 | TAS4-102-01 | mm | mA | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CL013 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (GW Radar) |  | S020NDA10CL013 | CCI-DAT-1461 | TBC | PRO-PID-12 | TAS4-103-01 | mm | mA | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CL014 | Separation Plant | TBC | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - |  |  |  | - | 0 to 5690 | 0 to 5690 | Level Transmitter (DP) |  | S020NDA10CL014 | CCI-DAT-1461 | TBC | PRO-PID-12 | TAS4-101-01 | mm | mA | MVar1: 0; MVar2: 1422.5; MVar3: 2845; MVar4: 4267.5; MVar5: 5690; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CL021 | Separation Plant | TBC | Rosemount 3051S2CD2A2B12A1BM5Q4Q8Q15 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (DP) |  | S020NDA10CL021 | CCI-DAT-1461 | TBC | PRO-PID-12 | TAS2-106-01 | mm | mA | MVar1: 335; MVar2: 1005; MVar3: 1675; MVar4: 2345; MVar5: 3015; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CL022 | Separation Plant | TBC | Rosemount 3051S2CD2A2B12A1BM5Q4Q8Q15 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (DP) |  | S020NDA10CL022 | CCI-DAT-1478 | TBC | PRO-PID-12 | TAS2-107-01 | mm | mA | MVar1: 335; MVar2: 1005; MVar3: 1675; MVar4: 2345; MVar5: 3015; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CL023 | Separation Plant | TBC | Rosemount 3051S2CD2A2B12A1BM5Q4Q8Q15 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (DP) |  | S020NDA10CL023 | CCI-DAT-1471 | TBC | PRO-PID-12 | TAS2-206-01 | mm | mA | MVar1: 335; MVar2: 1005; MVar3: 1675; MVar4: 2345; MVar5: 3015; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CL031 | Separation Plant | TBC | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM | - |  |  |  | 1676 | - | 335 to 3018 | Level Gauge |  | S020NDA10CL031 | CCI-DAT-1471 | TBC | PRO-PID-12 | 0 | mm | mm | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 0; IdO2: 670; IdO3: 1340; IdO4: 2010; IdO5: 2680
Tauhara B Steamfield | Separation Plant Production Piping System | 10CP010 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 17 | -1 to 55 | 0 to 23 | Pressure Indicating Transmitter |  | S020NDA10CP010 | CCI-DAT-1471 | TBC | PRO-PID-12 | TAS2-106-01 | bar(g) | mA | MVar1: 0; MVar2: 5.75; MVar3: 11.5; MVar4: 17.25; MVar5: 23; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CT010 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 217.9 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | S020NDA10CT010 | CCI-DAT-1461 | TBC | PRO-PID-11 | TAS2-205-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CT020 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 217.9 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | S020NDA10CT020 | CCI-DAT-1461 | TBC | PRO-PID-11 | TAS2-105-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 10CT030 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 217.9 | 0 to 250 | 0 to 250 | Temperature Indicating Transmitter |  | S020NDA10CT030 | CCI-DAT-1461 | TBC | PRO-PID-11 | TAS2-105-01 | °C | mA | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CF010 | Separation Plant | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 2530 | 0 to 3222 | 0 to 3222 | Flow Transmitter (Orifice Flow) |  | S020NDA20CF010 | CCI-DAT-1461 | TBC | PRO-PID-12 | TAS2-206-01 | tph | mA | MVar1: 0; MVar2: 805.5; MVar3: 1611; MVar4: 2416.5; MVar5: 3222; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CF020 | Separation Plant | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 2916 | 0 to 3222 | 0 to 3222 | Flow Transmitter (Orifice Flow) |  | S020NDA20CF020 | CCI-DAT-1461 | TBC | PRO-PID-12 | TAS2-302-01 | tph | mA | MVar1: 0; MVar2: 805.5; MVar3: 1611; MVar4: 2416.5; MVar5: 3222; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CL011 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (GW Radar) |  | S020NDA20CL011 | CCI-DAT-1461 | TBC | PRO-PID-13 | TAS4-101-01 | mm | mA | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CL012 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (GW Radar) |  | S020NDA20CL012 | CCI-DAT-1478 | TBC | PRO-PID-13 | TAS4-102-01 | mm | mA | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CL013 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (GW Radar) |  | S020NDA20CL013 | CCI-DAT-1471 | TBC | PRO-PID-13 | TAS4-103-01 | mm | mA | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CL014 | Separation Plant | TBC | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - |  |  |  | - | 0 to 5440 | 0 to 5440 | Level Transmitter (DP) |  | S020NDA20CL014 | CCI-DAT-1471 | TBC | PRO-PID-13 | TAS4-102-01 | mm | mA | MVar1: 0; MVar2: 1360; MVar3: 2720; MVar4: 4080; MVar5: 5440; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CL021 | Separation Plant | TBC | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (DP) |  | S020NDA20CL021 | CCI-DAT-1471 | TBC | PRO-PID-13 | TAS2-106-01 | mm | mA | MVar1: 335; MVar2: 1005; MVar3: 1675; MVar4: 2345; MVar5: 3015; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CL022 | Separation Plant | TBC | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (DP) |  | S020NDA20CL022 | CCI-DAT-1461 | TBC | PRO-PID-13 | TAS2-107-01 | mm | mA | MVar1: 335; MVar2: 1005; MVar3: 1675; MVar4: 2345; MVar5: 3015; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CL023 | Separation Plant | TBC | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (DP) |  | S020NDA20CL023 | CCI-DAT-1461 | TBC | PRO-PID-13 | TAS2-207-01 | mm | mA | MVar1: 335; MVar2: 1005; MVar3: 1675; MVar4: 2345; MVar5: 3015; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CL031 | Separation Plant | TBC | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM | - |  |  |  | 1676 | - | 335 to 3018 | Level Gauge |  | S020NDA20CL031 | CCI-DAT-1461 | TBC | PRO-PID-13 | 0 | mm | mm | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 0; IdO2: 670; IdO3: 1340; IdO4: 2010; IdO5: 2680
Tauhara B Steamfield | Separation Plant Production Piping System | 20CP010 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 9 | -1 to 55 | 0 to 15 | Pressure Indicating Transmitter |  | S020NDA20CP010 | CCI-DAT-1461 | TBC | PRO-PID-13 | TAS2-107-01 | bar(g) | mA | MVar1: 0; MVar2: 3.75; MVar3: 7.5; MVar4: 11.25; MVar5: 15; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CR001 | Separation Plant | TBC | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - |  |  |  | * | TBC | TBC | Corrosometer |  | S020NDA20CR001 | CCI-DAT-1461 | TBC | PRO-PID-12 | TAS4-104-01 | mm/Time Unit | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CR002 | Separation Plant | TBC | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - |  |  |  | * | TBC | TBC | Corrosometer |  | S020NDA20CR002 | CCI-DAT-1461 | TBC | PRO-PID-12 | TAS4-104-01 | mm/Time Unit | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CR003 | Separation Plant | TBC | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - |  |  |  | * | TBC | TBC | Corrosometer |  | S020NDA20CR003 | CCI-DAT-1469 | TBC | PRO-PID-12 | TAS4-104-01 | mm/Time Unit | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 20CR004 | Separation Plant | TBC | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - |  |  |  | * | TBC | TBC | Corrosometer |  | S020NDA30CR004 | CCI-DAT-1469 | TBC | PRO-PID-13 | TAS4-104-01 | mm/Time Unit | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 21CF010 | Separation Plant | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 450 | 0 to 495 | 0 to 495 | Flow Transmitter (Orifice Flow) |  | S020NDA21CF010 | CCI-DAT-1469 | TBC | PRO-PID-30 | TAS2-110-01 | l/m | mA | 0 | 123.75 | 247.5 | 371.25 | 495 |  |  | 4 | 8 | 12 | 16 | 20 |  |  |  |  | 15 | L/min
Tauhara B Steamfield | Separation Plant Production Piping System | 21CP010 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 17 | -1 to 55 | 0 to 25 | Pressure Indicating Transmitter |  | S020NDA21CP010 | CCI-DAT-1467 | TBC | PRO-PID-30 | TAS2-111-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 21CP011 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 18.8 | -1 to 55 | 0 to 25 | Pressure Indicating Transmitter |  | S020NDA21CP011 | CCI-DAT-1467 | TBC | PRO-PID-30 | TAS2-111-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 21CT010 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 202 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NDA21CT010 | CCI-DAT-1467 | TBC | PRO-PID-30 | TAS2-111-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 200
Tauhara B Steamfield | Separation Plant Production Piping System | 22CF020 | Separation Plant | TBC | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - |  |  |  | 450 | 0 to 495 | 0 to 495 | Flow Transmitter (Orifice Flow) |  | S020NDA22CF020 | CCI-DAT-1467 | TBC | PRO-PID-30 | TAS2-211-01 | l/m | mA | 0 | 123.75 | 247.5 | 371.25 | 495 |  |  | 4 | 8 | 12 | 16 | 20 |  |  |  |  | 15 | L/min
Tauhara B Steamfield | Separation Plant Production Piping System | 22CP020 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 17 | -1 to 55 | 0 to 25 | Pressure Indicating Transmitter |  | S020NDA22CP020 | CCI-DAT-1471 | TBC | PRO-PID-30 | TAS2-210-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 22CP021 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 18.8 | -1 to 55 | 0 to 25 | Pressure Indicating Transmitter |  | S020NDA22CP021 | CCI-DAT-1461 | TBC | PRO-PID-30 | TAS2-210-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 22CT020 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 202 | 0 to 250 | 0 to 250 | Temperature Element |  | S020NDA22CT020 | CCI-DAT-1465 | TBC | PRO-PID-30 | TAS2-211-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250; Digi1: 200
Tauhara B Steamfield | Separation Plant Production Piping System | 23CF011 | Separation Plant | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - |  |  |  | Refer to Specification | Refer to Specification | Refer to Specification | Flow Transmitter (Magnetic) |  | S020NDA23CF011 | CCI-DAT-1465 | TBC | PRO-PID-101 | TAS2-107-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 8 |  | 2
Tauhara B Steamfield | Separation Plant Production Piping System | 23CP511 | Separation Plant | TBC | Rosemount 3051CD3A02A1BS5M4Q4Q8T1Q15 | - |  |  |  | 0.23 | 0 to 20 | 0 to 20 | Pressure Differential Transmitter |  | S020NDA23CP511 | CCI-DAT-1465 | TBC | PRO-PID-101 | TAS2-107-01 | bar(g) | mA | MVar1: 0; MVar2: 5; MVar3: 10; MVar4: 15; MVar5: 20; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 2
Tauhara B Steamfield | Separation Plant Production Piping System | 23CP512 | Separation Plant | TBC | Wika 72039878+14503369+0731277 | - |  |  |  | 8 | 0 to 25 | - | Pressure Gauge |  | S020NDA23CP512 | CCI-DAT-1472 | TBC | PRO-PID-101 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 0; IdO2: 6.25; IdO3: 12.5; IdO4: 18.75; IdO5: 25
Tauhara B Steamfield | Separation Plant Production Piping System | 23CQ010 | Separation Plant | TBC | E+H CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 | - |  |  |  | 5 | 0 to 14 | 3.5 to 8.5 | Analyser Transmitter (pH) |  | S020NDA23CQ010 | PRO-CAL-0039 | TBC | PRO-PID-101 | TAS2-110-01 | pH | mA | 3.5 | 4.75 | 6 | 7.25 | 8.5 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 5.5 |  | 4.5
Tauhara B Steamfield | Separation Plant Production Piping System | 23CT011 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 60 | 0 to 215 | 0 to 100 | Temperature Indicating Transmitter |  | S020NDA23CT011 | CCI-DAT-1472 | TBC | PRO-PID-101 | TAS2-107-01 | °C | mA | 0 | 25 | 50 | 75 | 100 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 30 | 50
Tauhara B Steamfield | Separation Plant Production Piping System | 24CF020 | Separation Plant | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - |  |  |  | Refer to Specification | Refer to Specification | Refer to Specification | Flow Transmitter (Magnetic) |  | S020NDA24CF020 | PRO-CAL-0039 | TBC | PRO-PID-101 | TAS2-209-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 8 |  | 2
Tauhara B Steamfield | Separation Plant Production Piping System | 24CP521 | Separation Plant | TBC | Rosemount 3051CD3A02A1BS5M4Q4Q8T1Q15 | - |  |  |  | 0.23 | 0 to 20 | 0 to 20 | Pressure Differential Transmitter |  | S020NDA24CP521 | CCI-DAT-1469 | TBC | PRO-PID-101 | TAS2-207-01 | bar(g) | mA | MVar1: 0; MVar2: 5; MVar3: 10; MVar4: 15; MVar5: 20; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 2
Tauhara B Steamfield | Separation Plant Production Piping System | 24CP522 | Separation Plant | TBC | Wika 72039878+14503369+0731277 | - |  |  |  | 8 | 0 to 25 | - | Pressure Gauge |  | S020NDA24CP522 | CCI-DAT-1469 | TBC | PRO-PID-101 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 0; IdO2: 6.25; IdO3: 12.5; IdO4: 18.75; IdO5: 25
Tauhara B Steamfield | Separation Plant Production Piping System | 24CQ020 | Separation Plant | TBC | E+H CM442-EL64/0 + CPS47E-10C2/0 | - |  |  |  | 5 | 0 to 14 | 3.5 to 8.5 | Analyser Transmitter (pH) |  | S020NDA24CQ020 | CCI-DAT-1469 | TBC | PRO-PID-101 | TAS2-209-01 | pH | mA | 3.5 | 4.75 | 6 | 7.25 | 8.5 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 5.5 |  | 4.5
Tauhara B Steamfield | Separation Plant Production Piping System | 24CT021 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 60 | 0 to 215 | 0 to 100 | Temperature Indicating Transmitter |  | S020NDA24CT021 | CCI-DAT-1467 | TBC | PRO-PID-101 | TAS2-207-01 | °C | mA | 0 | 25 | 50 | 75 | 100 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 30 | 50
Tauhara B Steamfield | Separation Plant Production Piping System | 30CL011 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (GW Radar) |  | S020NDA30CL011 | CCI-DAT-1467 | TBC | PRO-PID-14 | TAS4-101-01 | mm | mA | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 30CL012 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (GW Radar) |  | S020NDA30CL012 | CCI-DAT-1467 | TBC | PRO-PID-14 | TAS4-102-01 | mm | mA | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 30CL013 | Separation Plant | TBC | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (GW Radar) |  | S020NDA30CL013 | CCI-DAT-1467 | TBC | PRO-PID-14 | TAS4-103-01 | mm | mA | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 30CL014 | Separation Plant | TBC | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - |  |  |  | - | 0 to 5640 | 0 to 5640 | Level Transmitter (DP) |  | S020NDA30CL014 | CCI-DAT-1471 | TBC | PRO-PID-14 | TAS4-103-01 | mm | mA | MVar1: 0; MVar2: 1410; MVar3: 2820; MVar4: 4230; MVar5: 5640; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 30CL015 | Separation Plant | TBC | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - |  |  |  | - | 0 to 5640 | 0 to 5640 | Level Transmitter (DP) |  | S020NDA30CL015 | CCI-DAT-1461 | TBC | PRO-PID-14 | TAS4-104-01 | mm | mA | MVar1: 0; MVar2: 1410; MVar3: 2820; MVar4: 4230; MVar5: 5640; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 30CL021 | Separation Plant | TBC | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (DP) |  | S020NDA30CL021 | COSASCO | TBC | PRO-PID-14 | TAS2-108-01 | mm | mA | MVar1: 335; MVar2: 1005; MVar3: 1675; MVar4: 2345; MVar5: 3015; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 30CL022 | Separation Plant | TBC | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (DP) |  | S020NDA30CL022 | Model 3500/3500HT | TBC | PRO-PID-14 | TAS2-109-01 | mm | mA | MVar1: 335; MVar2: 1005; MVar3: 1675; MVar4: 2345; MVar5: 3015; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 30CL023 | Separation Plant | TBC | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - |  |  |  | 1676 | 0 to 2680 | 335 to 3015 | Level Transmitter (DP) |  | S020NDA30CL023 | ER-420 | TBC | PRO-PID-14 | TAS2-208-01 | mm | mA | MVar1: 335; MVar2: 1005; MVar3: 1675; MVar4: 2345; MVar5: 3015; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 30CL031 | Separation Plant | TBC | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM | - |  |  |  | 1676 | - | 335 to 3018 | Level Gauge |  | S020NDA30CL031 | COSASCO | TBC | PRO-PID-14 | 0 | mm | mm | MVar1: 0; MVar2: 670; MVar3: 1340; MVar4: 2010; MVar5: 2680; IdO1: 0; IdO2: 670; IdO3: 1340; IdO4: 2010; IdO5: 2680
Tauhara B Steamfield | Separation Plant Production Piping System | 30CP011 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NDA30CP011 | Model 3500/3500HT | TBC | PRO-PID-14 | TAS2-108-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping System | 30CP012 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 1 | -1 to 10.3 | 0 to 5 | Pressure Indicating Transmitter |  | S020NDA30CP012 | ER-420 | TBC | PRO-PID-14 | TAS2-208-01 | bar(g) | mA | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Separated Water System | 10CP010 | Separation Plant | TBC | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 2.6 | -1 to 10.3 | 0 to 10 | Pressure Indicating Transmitter |  | S020NDB10CP010 | COSASCO | TBC | PRO-PID-26 | TAS3 104-01 | bar(g) | mA | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Separated Water System | 11CF011 | Separation Plant | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - |  |  |  | Refer to Specification | Refer to Specification | 0 to 10 | Flow Transmitter (Magnetic) |  | S020NDB11CF011 | Model 3500/3500HT | TBC | PRO-PID-100 | TAS2-111-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 8 |  | 2
Tauhara B Steamfield | Separation Plant Separated Water System | 11CQ010 | Separation Plant | TBC | E+H CM442-EL64/0 + CPS47E-10C2/0 | - |  |  |  | 5 | 0 to 14 | 3.5 to 8.5 | Analyser Transmitter (pH) |  | S020NDB11CQ010 | ER-420 | TBC | PRO-PID-100 | TAS2-110-01 | pH | mA | MVar1: 3.5; MVar2: 4.75; MVar3: 6; MVar4: 7.25; MVar5: 8.5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Separated Water System | 11CT011 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 60 | 0 to 75 | 0 to 100 | Temperature Indicating Transmitter |  | S020NDB11CT011 | COSASCO | TBC | PRO-PID-100 | TAS2-108-01 | °C | mA | 0 | 25 | 50 | 75 | 100 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 30 | 50
Tauhara B Steamfield | Separation Plant Separated Water System | 12CF021 | Separation Plant | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - |  |  |  | Refer to Specification | Refer to Specification | Refer to Specification | Flow Transmitter (Magnetic) |  | S020NDB12CF021 | Model 3500/3500HT | TBC | PRO-PID-100 | TAS2-210-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 8 |  | 2
Tauhara B Steamfield | Separation Plant Separated Water System | 12CQ020 | Separation Plant | TBC | E+H CM442-EL64/0 + CPS47E-10C2/0 | - |  |  |  | 5 | 0 to 14 | 3.5 to 8.5 | Analyser Transmitter (pH) |  | S020NDB12CQ020 | ER-420 | TBC | PRO-PID-100 | TAS2-210-01 | pH | mA | MVar1: 3.5; MVar2: 4.75; MVar3: 6; MVar4: 7.25; MVar5: 8.5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Separated Water System | 12CT021 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 60 | 0 to 75 | 0 to 100 | Temperature Indicating Transmitter |  | S020NDB12CT021 | CCI-DAT-1472 | TBC | PRO-PID-100 | TAS2-208-01 | °C | mA | 0 | 25 | 50 | 75 | 100 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 30 | 50
Tauhara B Steamfield | Separation Plant Separated Water System | 13CF031 | Separation Plant | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - |  |  |  | Refer to Specification | Refer to Specification | Refer to Specification | Flow Transmitter (Magnetic) |  | S020NDB13CF031 | PRO-CAL-0039 | TBC | PRO-PID-100 | TAS2-211-01 | l/m | mA | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 8 |  | 2
Tauhara B Steamfield | Separation Plant Separated Water System | 13CQ030 | Separation Plant | TBC | E+H CM442-EL64/0 | - |  |  |  | 5 | 0 to 14 | 3.5 to 8.5 | Analyser Transmitter (pH) |  | S020NDB13CQ030 | CCI-DAT-1461 | TBC | PRO-PID-100 | TAS2-211-01 | pH | mA | MVar1: 3.5; MVar2: 4.75; MVar3: 6; MVar4: 7.25; MVar5: 8.5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Separated Water System | 13CT031 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 60 | 0 to 75 | 0 to 100 | Temperature Indicating Transmitter |  | S020NDB13CT031 | CCI-DAT-1461 | TBC | PRO-PID-100 | TAS2-208-01 | °C | mA | 0 | 25 | 50 | 75 | 100 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 30 | 50
Tauhara B Steamfield | Separation Plant Separated Water System | 14CF041 | Separation Plant | TBC | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - |  |  |  | Refer to Specification | Refer to Specification | Refer to Specification | Flow Transmitter (Magnetic) |  | S020NDB14CF041 | CCI-DAT-1466 | TBC | PRO-PID-100 | TAS2-108-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 8 |  | 2
Tauhara B Steamfield | Separation Plant Separated Water System | 14CQ040 | Separation Plant | TBC | E+H CM442-EL64/0 | - |  |  |  | 5 | 0 to 14 | 3.5 to 8.5 | Analyser Transmitter (pH) |  | S020NDB14CQ040 | CCI-DAT-1472 | TBC | PRO-PID-100 | TAS2-108-01 | pH | mA | MVar1: 3.5; MVar2: 4.75; MVar3: 6; MVar4: 7.25; MVar5: 8.5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Separated Water System | 14CT041 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 60 | 0 to 75 | 0 to 100 | Temperature Indicating Transmitter |  | S020NDB14CT041 | PRO-CAL-0039 | TBC | PRO-PID-100 | TAS2-108-01 | °C | mA | 0 | 25 | 50 | 75 | 100 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 30 | 50
Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CL010 | Separation Plant | TBC | Vega PS31.XXXXXGMHB +GFLK.ADGX | - |  |  |  | N/A | 0 to 4500 | TBC | Level Transmitter (Radar) |  | S020QCM10CL010 | CCI-DAT-1461 | TBC | PRO-PID-29 | TAS2-110-01 | mm | mA | 0 | 1125 | 2250 | 3375 | 4500 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 95 | 95 | 10
Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CL020 | Separation Plant | TBC | Vega PS31.XXXXXGMHB +GFLK.ADGX | - |  |  |  | N/A | 0 to 4500 | TBC | Level Transmitter (Radar) |  | S020QCM10CL020 | CCI-DAT-1461 | TBC | PRO-PID-29 | TAS2-210-01 | mm | mA | 0 | 1125 | 2250 | 3375 | 4500 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 95 | 95 | 10
Tauhara B Steamfield | Separation Plant Acid Dosing System | 10DL0020 | Separation Plant | TBC | Vega TKALM3-HMI-DB | - |  |  |  | N/A | See notes | 0-100% | Level Indicator (Remote) |  | S020QCM10DL0020 | QCM-PRO-SPC-0109 | TBC | PRO-PID-29 | LEVEL INDICATOR REMOTE | mm | mA | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 10EH011 | Separation Plant | TBC | Vega See S020QCM10DL0020 | - |  |  |  | N/A | N/A | N/A | Level Sounder Beacon (Remote) |  | S020QCM10EH011 | QCM-PRO-SPC-0109 | TBC | PRO-PID-29 | 0 | mm | - | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CF010 | Separation Plant | TBC | Yokogawa AX005-GA000BA2AT224B-2JA11/GRT | - |  |  |  | 2.2 | 0-3 | 0 to 2.5 | Flow Transmitter (Magnetic) |  | S020QCM20CF010 | QCM-PRO-SPC-0109 | TBC | PRO-PID-30 | TAS2-110-01 | l/m | mA | 0 | 0.625 | 1.25 | 1.875 | 2.5 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 2 |  | 0.5
Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CP011 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 18.4 | -1 to 55 | 0 to 30 | Pressure Indicating Transmitter |  | S020QCM20CP011 | QCM-PRO-SPC-0109 | TBC | PRO-PID-30 | TAS2-110-01 | bar(g) | mA | MVar1: 0; MVar2: 7.5; MVar3: 15; MVar4: 22.5; MVar5: 30; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 27
Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CP501 | Separation Plant | TBC | Wika 72039899+14503369+ | - |  |  |  | 0.3 | 0 to 5 | - | Pressure Gauge |  | S020QCM20CP501 | QCM-PRO-SPC-0109 | TBC | PRO-PID-30 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 0; IdO2: 1.25; IdO3: 2.5; IdO4: 3.75; IdO5: 5
Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CP510 | Separation Plant | TBC | Wika 72039915 (Model 433.56.100)+14503369 (Model IV10)+ | - |  |  |  | 18.4 | 0 to 40 | - | Pressure Gauge |  | S020QCM20CP510 | QCM-PRO-SPC-0109 | TBC | PRO-PID-30 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40; IdO1: 0; IdO2: 10; IdO3: 20; IdO4: 30; IdO5: 40
Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CT010 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 20 | -5 to 50 | -5 to 50 | Temperature Element |  | S020QCM20CT010 | QCM-PRO-SPC-0109 | TBC | PRO-PID-30 | TAS2-101-01 | °C | °C | MVar1: -5; MVar2: 8.75; MVar3: 22.5; MVar4: 36.25; MVar5: 50; IdO1: -5; IdO2: 8.75; IdO3: 22.5; IdO4: 36.25; IdO5: 50
Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CF010 | Separation Plant | TBC | IFM SI5004+E40107 | - |  |  |  | 2.2 | 0-3 | 0 to 2.5 | Flow Transmitter (Magnetic) |  | S020QCM21CF010 | QCM-PRO-SPC-0109 | TBC | PRO-PID-30 | 0 | l/m | mA | MVar1: 0; MVar2: 0.625; MVar3: 1.25; MVar4: 1.875; MVar5: 2.5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CF020 | Separation Plant | TBC | IFM SI5004+E40107 | - |  |  |  | 2.2 | 0-3 | 0 to 2.5 | Flow Transmitter (Magnetic) |  | S020QCM21CF020 | QCM-PRO-SPC-0109 | TBC | PRO-PID-30 | 0 | l/m | mA | MVar1: 0; MVar2: 0.625; MVar3: 1.25; MVar4: 1.875; MVar5: 2.5; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CP021 | Separation Plant | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 18.4 | -1 to 55 | 0 to 30 | Pressure Indicating Transmitter |  | S020QCM21CP021 | CCI-DAT-1469 | TBC | PRO-PID-30 | TAS2-210-01 | bar(g) | mA | MVar1: 0; MVar2: 7.5; MVar3: 15; MVar4: 22.5; MVar5: 30; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 27
Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CP502 | Separation Plant | TBC | Wika 72039899+14503369+ | - |  |  |  | 0.3 | 0 to 5 | - | Pressure Gauge |  | S020QCM21CP502 | CCI-DAT-1469 | TBC | PRO-PID-30 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 1.25; MVar3: 2.5; MVar4: 3.75; MVar5: 5; IdO1: 0; IdO2: 1.25; IdO3: 2.5; IdO4: 3.75; IdO5: 5
Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CP520 | Separation Plant | TBC | Wika 72039915 (Model 433.56.100)+14503369 (Model IV10)+ | - |  |  |  | 18.4 | 0 to 40 | - | Pressure Gauge |  | S020QCM21CP520 | CCI-DAT-1469 | TBC | PRO-PID-30 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40; IdO1: 0; IdO2: 10; IdO3: 20; IdO4: 30; IdO5: 40
Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CT020 | Separation Plant | TBC | Rosemount 644HANAJ1M4Q4T1 | - |  |  |  | 20 | -5 to 50 | -5 to 50 | Temperature Element |  | S020QCM21CT020 | CCI-DAT-1467 | TBC | PRO-PID-30 | TAS2-201-01 | °C | °C | MVar1: -5; MVar2: 8.75; MVar3: 22.5; MVar4: 36.25; MVar5: 50; IdO1: -5; IdO2: 8.75; IdO3: 22.5; IdO4: 36.25; IdO5: 50
Tauhara B Steamfield | Separation Plant Acid Dosing System | 30CL031 | Separation Plant | TBC | Vega PS21.XXXXXGMHB+MBA.BB | - |  |  |  | N/A | 0 to 1500 | 0 to 1500 | Level Transmitter (Radar) |  | S020QCM30CL031 | CCI-DAT-1467 | TBC | PRO-PID-29 | TAS2-110-01 | mm | mA | MVar1: 0; MVar2: 375; MVar3: 750; MVar4: 1125; MVar5: 1500; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 30CL032 | Separation Plant | TBC | Vega PS21.XXXXXGMHB+MBA.BB | - |  |  |  | N/A | 0 to 1500 | 0 to 1500 | Level Transmitter (Radar) |  | S020QCM30CL032 | CCI-DAT-1467 | TBC | PRO-PID-29 | TAS2-210-01 | mm | mA | MVar1: 0; MVar2: 375; MVar3: 750; MVar4: 1125; MVar5: 1500; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing System | 30CQ010 | Separation Plant | TBC | E+H CLS50D-1009/0 + CYA112-1V02/0 | - |  |  |  | TBC | TBC | TBC | Analyser Transmitter (Conductivity) |  | S020QCM30CQ010 | CCI-DAT-1467 | TBC | PRO-PID-29 | TAS2-110-01 | uS/cm | mA | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Fire Water | 10CP401 | Pump Station | TBC | Wika 72039878+14503369 | - |  |  |  | - | 0 to 16 | - | Pressure Gauge |  | S020SGA10CP401 | CCI-DAT-1467 | TBC | PRO-PID-50 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Pump Station Fire Water | 10CP402 | Pump Station | TBC | Wika 72039878+14503369 | - |  |  |  | - | 0 to 16 | - | Pressure Gauge |  | S020SGA10CP402 | CCI-DAT-1471 | TBC | PRO-PID-50 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Pump Station Fire Water | 10CP405 | Pump Station | TBC | Wika 72039878+14503369 | - |  |  |  | - | 0 to 16 | - | Pressure Gauge |  | S020SGA10CP405 | CCI-DAT-1461 | TBC | PRO-PID-50 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Pump Station Fire Water | 10CP406 | Pump Station | TBC | Wika 72039878+14503369 | - |  |  |  | - | 0 to 16 | - | Pressure Gauge |  | S020SGA10CP406 | CCI-DAT-1461 | TBC | PRO-PID-50 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 4; MVar3: 8; MVar4: 12; MVar5: 16; IdO1: 0; IdO2: 4; IdO3: 8; IdO4: 12; IdO5: 16
Tauhara B Steamfield | Separation Plant Room Temperature | 10CT001 | Separation Plant | TBC | E+H TST434-J1A3B0 | - |  |  |  | - | TBC | TBC | Temperature Element |  | S020SAA10CT001 | CCI-DAT-1461 | TBC | - | TAS2-104-01 | °C | °C | MVar1: -50; MVar2: -25; MVar3: 0; MVar4: 25; MVar5: 50; IdO1: -50; IdO2: -25; IdO3: 0; IdO4: 25; IdO5: 50
Tauhara B Steamfield | Separation Plant Room Temperature | 10CT002 | Separation Plant | TBC | E+H TST434-J1A3B0 | - |  |  |  | - | TBC | TBC | Temperature Element |  | S020SAA10CT002 | QCM-PRO-SPC-0109 | TBC | - | TAS2-104-01 | °C | °C | MVar1: -50; MVar2: -25; MVar3: 0; MVar4: 25; MVar5: 50; IdO1: -50; IdO2: -25; IdO3: 0; IdO4: 25; IdO5: 50
Tauhara B Steamfield | Separation Plant Room Temperature | 10CT003 | Separation Plant | TBC | E+H TST434-J1A3B0 | - |  |  |  | - | TBC | TBC | Temperature Element |  | S020SAA10CT003 | QCM-PRO-DAT-0108 | TBC | - | TAS2-104-01 | °C | °C | MVar1: -50; MVar2: -25; MVar3: 0; MVar4: 25; MVar5: 50; IdO1: -50; IdO2: -25; IdO3: 0; IdO4: 25; IdO5: 50
Tauhara B Steamfield | Pump Station Room Temperature | 10CT001 | Pump Station | TBC | E+H TST434-J1A3B0 | - |  |  |  | - | TBC | TBC | Temperature Element |  | P020SAA10CT001 | QCM-PRO-SPC-0109 | TBC | - | TAS3-201-01 | °C | °C | MVar1: -50; MVar2: -25; MVar3: 0; MVar4: 25; MVar5: 50; IdO1: -50; IdO2: -25; IdO3: 0; IdO4: 25; IdO5: 50
Tauhara B Steamfield | Pump Station Room Temperature | 10CT002 | Pump Station | TBC | E+H TST434-J1A3B0 | - |  |  |  | - | TBC | TBC | Temperature Element |  | P020SAA10CT002 | QCM-PRO-SPC-0109 | TBC | - | TAS3-201-01 | °C | °C | MVar1: -50; MVar2: -25; MVar3: 0; MVar4: 25; MVar5: 50; IdO1: -50; IdO2: -25; IdO3: 0; IdO4: 25; IdO5: 50
Tauhara B Steamfield | Pump Station Room Temperature | 10CT003 | Pump Station | TBC | E+H TST434-J1A3B0 | - |  |  |  | - | TBC | TBC | Temperature Element |  | P020SAA10CT003 | QCM-PRO-SPC-0109 | TBC | - | TAS3-201-01 | °C | °C | MVar1: -50; MVar2: -25; MVar3: 0; MVar4: 25; MVar5: 50; IdO1: -50; IdO2: -25; IdO3: 0; IdO4: 25; IdO5: 50
Tauhara B Steamfield | Pump Station Room Temperature | 10CT004 | Pump Station | TBC | E+H TST434-J1A3B0 | - |  |  |  | - | TBC | TBC | Temperature Element |  | P020SAA10CT004 | QCM-PRO-SPC-0109 | TBC | - | TAS3-201-01 | °C | °C | MVar1: -50; MVar2: -25; MVar3: 0; MVar4: 25; MVar5: 50; IdO1: -50; IdO2: -25; IdO3: 0; IdO4: 25; IdO5: 50
Tauhara B Steamfield | TH11 110VDC System - Voltage Battery Systems | 10CE101 | TH11 110VDC System - Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | 0110BTL10CE101 | QCM-PRO-SPC-0109 | TBC | - | TH11-7.5-002-01 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | TH11 110VDC System - Current Battery Systems | 10CE201 | TH11 110VDC System - Current | Indication | TBC | C |  |  |  | - | 0 to 150 A | 0 to 150 A | - |  | 0110BTL10CE201 | QCM-PRO-SPC-0109 | TBC | - | TH11-7.5-002-01 | Amps | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH12 110VDC System - Voltage Battery Systems | 10CE101 | TH12 110VDC System - Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | 0120BTL10CE101 | QCM-PRO-SPC-0109 | TBC | - | TH12-8.5-003-01 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | TH12 110VDC System - Current Battery Systems | 10CE201 | TH12 110VDC System - Current | Indication | TBC | C |  |  |  | - | 0 to 150 A | 0 to 150 A | - |  | 0120BTL10CE201 | QCM-PRO-SPC-0109 | TBC | - | TH12-8.5-003-01 | Amps | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH26 110VDC System - Voltage Battery Systems | 10CE101 | TH26 110VDC System - Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | 0260BTL10CE101 | QCM-PRO-SPC-0109 | TBC | - | TH26-4.5-003-01 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | TH26 110VDC System - Current Battery Systems | 10CE201 | TH26 110VDC System - Current | Indication | TBC | C |  |  |  | - | 0 to 150 A | 0 to 150 A | - |  | 0260BTL10CE201 | QCM-PRO-SPC-0109 | TBC | - | TH26-4.5-003-01 | Amps | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH28 110VDC System - Voltage Battery Systems | 10CE101 | TH28 110VDC System - Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | 0280BTL10CE101 | CCI-DAT-1468 | TBC | - | TH28-9.5-003-01 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | TH28 110VDC System - Current Battery Systems | 10CE201 | TH28 110VDC System - Current | Indication | TBC | C |  |  |  | - | 0 to 150 A | 0 to 150 A | - |  | 0280BTL10CE201 | CCI-DAT-1468 | TBC | - | TH28-9.5-003-01 | Amps | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH29 110VDC System - Voltage Battery Systems | 10CE101 | TH29 110VDC System - Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | 0290BTL10CE101 | CCI-DAT-1466 | TBC | - | TH29-2.5-004-01 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | TH29 110VDC System - Current Battery Systems | 10CE201 | TH29 110VDC System - Current | Indication | TBC | C |  |  |  | - | 0 to 150 A | 0 to 150 A | - |  | 0290BTL10CE201 | CCI-DAT-1470 | TBC | - | TH29-2.5-004-01 | Amps | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH37 110VDC System - Voltage Battery Systems | 10CE101 | TH37 110VDC System - Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | 0370BTL10CE101 |  | TBC | - | TAS1-3.5-004-02 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | TH37 110VDC System - Current Battery Systems | 10CE201 | TH37 110VDC System - Current | Indication | TBC | C |  |  |  | - | 0 to 150 A | 0 to 150 A | - |  | 0370BTL10CE201 | CCI-DAT-1474 | TBC | - | TAS1-3.5-004-02 | Amps | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SGW 230VAC Inverter A Output Voltage Battery Systems | 10CE101 | SGW 230VAC Inverter A Output Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 300 V | 0 to 300 V | - |  | P020BRA10CE101 | CCI-DAT-1461 | TBC | - | TAS3-502-01 | Volts | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 215
Tauhara B Steamfield | SGW 230VAC Inverter A Output Current Battery Systems | 10CE201 | SGW 230VAC Inverter A Output Current | Indication | TBC | C |  |  |  | - | 0 to 40 A | 0 to 40 A | - |  | P020BRA10CE201 | CCI-DAT-1460 | TBC | - | TAS3-502-01 | Amps | mA | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SGW 230VAC Inverter B Output Voltage Battery Systems | 10CE101 | SGW 230VAC Inverter B Output Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 300 V | 0 to 300 V | - |  | P020BRB10CE101 | CCI-DAT-1460 | TBC | - | TAS3-602-01 | Volts | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 215
Tauhara B Steamfield | SGW 230VAC Inverter B Output Current Battery Systems | 10CE201 | SGW 230VAC Inverter B Output Current | Indication | TBC | C |  |  |  | - | 0 to 40 A | 0 to 40 A | - |  | P020BRB10CE201 | CCI-DAT-1466 | TBC | - | TAS3-602-01 | Amps | mA | MVar1: 0; MVar2: 10; MVar3: 20; MVar4: 30; MVar5: 40; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SGW 110VDC System A Output Voltage Battery Systems | 10CE101 | SGW 110VDC System A Output Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | P020BTL10CE101 | CCI-DAT-1474 | TBC | - | TAS3-502-01 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | SGW 110VDC System A Output current Battery Systems | 10CE201 | SGW 110VDC System A Output current | Indication | TBC | C |  |  |  | - | 0 to 150 A | 0 to 150 A | - |  | P020BTL10CE201 | CCI-DAT-1474 | TBC | - | TAS3-502-01 | Amps | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SGW 110VDC System B Output Voltage Battery Systems | 10CE101 | SGW 110VDC System B Output Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | P020BTM10CE101 | CCI-DAT-1474 | TBC | - | TAS3-602-01 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | SGW 110VDC System B Output current Battery Systems | 10CE201 | SGW 110VDC System B Output current | Indication | TBC | C |  |  |  | - | 0 to 100A | 0 to 100A | - |  | P020BTM10CE201 | CCI-DAT-1461 | TBC | - | TAS3-602-01 | Amps | mA | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SP 230VAC Inverter A Output Voltage Battery Systems | 10CE101 | SP 230VAC Inverter A Output Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 300 V | 0 to 300 V | - |  | S020BRA10CE101 | CCI-DAT-1460 | TBC | - | TAS2-502-01 | Volts | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 215
Tauhara B Steamfield | SP 230VAC Inverter B Output Voltage Battery Systems | 10CE201 | SP 230VAC Inverter B Output Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 300 V | 0 to 300 V | - |  | S020BRA10CE201 | CCI-DAT-1460 | TBC | - | TAS2-602-01 | Volts | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 215
Tauhara B Steamfield | SP 110VDC System A Output Voltage Battery Systems | 10CE101 | SP 110VDC System A Output Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | S020BTL10CE101 | CCI-DAT-1466 | TBC | - | TAS2-502-01 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | SP 110VDC System B Output Voltage Battery Systems | 10CE101 | SP 110VDC System B Output Voltage | Alarm & Indication | TBC | C |  |  |  | - | 0 to 150 V | 0 to 150 V | - |  | S020BTM10CE101 | CCI-DAT-1468 | TBC | - | TAS2-602-01 | Volts | mA | MVar1: 0; MVar2: 37.5; MVar3: 75; MVar4: 112.5; MVar5: 150; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20; Digi1: 100
Tauhara B Steamfield | SP 230VAC Inverter B Output Voltage Battery Systems | 10CE101 | SP 230VAC Inverter B Output Voltage | Alarm & Indication | TBC | - |  |  |  | - | 0 to 300 V | 0 to 300 V | - |  | S020BRB10CE101 | CCI-DAT-1468 | TBC | - | TAS2-602-01 | Volts | mA | MVar1: 0; MVar2: 75; MVar3: 150; MVar4: 225; MVar5: 300; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH11 24Vdc Comms DCS Power Supplies | 10CE101 | PLC Cabinet TH11 24Vdc Comms | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0110CRA10CE101 | See notes | TBC | - | TH11-7.5-002-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH11 24Vdc IO DCS Power Supplies | 10CE102 | PLC Cabinet TH11 24Vdc IO | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0110CRA10CE102 | CCI-DAT-1460 | TBC | - | TH11-7.5-002-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH12 24Vdc Comms DCS Power Supplies | 10CE101 | PLC Cabinet TH12 24Vdc Comms | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0120CRA10CE101 | CCI-DAT-1460 | TBC | - | TH12-8.5-003-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH12 24Vdc IO DCS Power Supplies | 10CE102 | PLC Cabinet TH12 24Vdc IO | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0120CRA10CE102 | CCI-DAT-1460 | TBC | - | TH12-8.5-003-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH26 24Vdc Comms DCS Power Supplies | 10CE101 | PLC Cabinet TH26 24Vdc Comms | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0260CRA10CE101 | CCI-DAT-1460 | TBC | - | TH26-4.5-003-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH26 24Vdc IO DCS Power Supplies | 10CE201 | PLC Cabinet TH26 24Vdc IO | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0260CRA10CE201 | CCI-DAT-1466 | TBC | - | TH26-4.5-003-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH28 24Vdc Comms DCS Power Supplies | 10CE101 | PLC Cabinet TH28 24Vdc Comms | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0280CRA10CE101 | CCI-DAT-1466 | TBC | - | TH28-9.5-003-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH28 24Vdc IO DCS Power Supplies | 10CE201 | PLC Cabinet TH28 24Vdc IO | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0280CRA10CE201 | CCI-DAT-1466 | TBC | - | TH28-9.5-003-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH29 24Vdc Comms DCS Power Supplies | 10CE101 | PLC Cabinet TH29 24Vdc Comms | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0290CRA10CE101 | CCI-DAT-1466 | TBC | - | TH29-2.5-004-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH29 24Vdc IO DCS Power Supplies | 10CE201 | PLC Cabinet TH29 24Vdc IO | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0290CRA10CE201 | CCI-DAT-1466 | TBC | - | TH29-2.5-004-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH37 24Vdc Comms DCS Power Supplies | 10CE101 | PLC Cabinet TH37 24Vdc Comms | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0370CRA10CE101 | CCI-DAT-1466 | TBC | - | TAS1-3.5-003-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TH37 24Vdc IO DCS Power Supplies | 10CE201 | PLC Cabinet TH37 24Vdc IO | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | 0370CRA10CE201 | CCI-DAT-1466 | TBC | - | TAS1-3.5-003-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS3 24Vdc DCS Power Supplies | 10CE101 | PLC Cabinet TAS3 24Vdc | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA10CE101 | - | TBC | - | TAS3-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 1 24Vdc DCS Power Supplies | 10CE102 | PLC Cabinet TAS3 Cluster 1 24Vdc | Alarm & Indication | TBC | C |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA10CE102 | - | TBC | - | TAS3-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 2 24Vdc DCS Power Supplies | 10CE103 | PLC Cabinet TAS3 Cluster 2 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA10CE103 | - | TBC | - | TAS3-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 3 24Vdc DCS Power Supplies | 10CE104 | PLC Cabinet TAS3 Cluster 3 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA10CE104 | - | TBC | - | TAS3-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 4 24Vdc DCS Power Supplies | 10CE105 | PLC Cabinet TAS3 Cluster 4 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA10CE105 | - | TBC | - | TAS3-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 5 24Vdc DCS Power Supplies | 10CE106 | PLC Cabinet TAS3 Cluster 5 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA10CE106 | - | TBC | - | TAS3-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 6 24Vdc DCS Power Supplies | 10CE107 | PLC Cabinet TAS3 Cluster 6 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA10CE107 | - | TBC | - | TAS3-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS3 Vibration Rack 24Vdc DCS Power Supplies | 10CE109 | PLC Cabinet TAS3 Vibration Rack 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA10CE109 | - | TBC | - | TAS3-601-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Server Cabinet NSP 24Vdc DCS Power Supplies | 10CE101 | Server Cabinet NSP 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRS10CE101 | - | TBC | - | TAS3-601-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Server Cabinet BLDG Services 24Vdc DCS Power Supplies | 10CE102 | Server Cabinet BLDG Services 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRS10CE102 | - | TBC | - | TAS3-601-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS1 24Vdc DCS Power Supplies | 20CE101 | PLC Cabinet TAS1 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA20CE101 | - | TBC | - | TAS2-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS2 24Vdc DCS Power Supplies | 30CE101 | PLC Cabinet TAS2 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA30CE101 | - | TBC | - | TAS2-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 1 24Vdc DCS Power Supplies | 30CE102 | PLC Cabinet TAS2 Cluster 1 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | P020CRA30CE102 | - | TBC | - | TAS2-501-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 2 24Vdc DCS Power Supplies | 30CE103 | PLC Cabinet TAS2 Cluster 2 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | - | - | - |  | P020CRA30CE103 | - | TBC | - | TAS2-501-01 | - | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 3 24Vdc DCS Power Supplies | 30CE104 | PLC Cabinet TAS2 Cluster 3 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | - | - | - |  | P020CRA30CE104 | - | TBC | - | TAS2-501-01 | - | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 4 24Vdc DCS Power Supplies | 30CE105 | PLC Cabinet TAS2 Cluster 4 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | - | - | - |  | P020CRA30CE105 | - | TBC | - | TAS2-501-01 | - | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 5 24Vdc DCS Power Supplies | 30CE106 | PLC Cabinet TAS2 Cluster 5 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | - | - | - |  | P020CRA30CE106 | - | TBC | - | TAS2-501-01 | - | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 6 24Vdc DCS Power Supplies | 30CE107 | PLC Cabinet TAS2 Cluster 6 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | - | - | - |  | P020CRA30CE107 | - | TBC | - | TAS2-501-01 | - | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | Server Cabinet NSP 24Vdc DCS Power Supplies | 20CE101 | Server Cabinet NSP 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | S020CRS20CE101 | - | TBC | - | TAS2-601-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Server Cabinet Build Services 24Vdc DCS Power Supplies | 40CE101 | Server Cabinet Build Services 24Vdc | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 VDC | 0 to 50 VDC | - |  | S020CRS40CE101 | - | TBC | - | TAS2-601-01 | Volts | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump | 10CP010 | Wellpad TH28 | Alarm & Indication | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - |  |  |  | 0 | -1 to 10.3 | 0 to 10 | Pressure Gauge |  | 0280LFC10CP010 | - | TBC | PRO-PID-31 | TH28-9.5.002-01 | bar(g) | mA | MVar1: 0; MVar2: 2.5; MVar3: 5; MVar4: 7.5; MVar5: 10; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad LCP (LCP2-1) Separated Water | 10CP501 | Wellpad LCP (LCP2-1) | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0320NDB10CP501 | - | TBC | PRO-PID-38 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad LCP (LCP2-1) Separated Water | 10CP520 | Wellpad LCP (LCP2-1) | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0320NDB10CP520 | - | TBC | PRO-PID-38 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad LCP (LCP2-2) Separated Water | 10CP510 | Wellpad LCP (LCP2-2) | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0330NDB10CP510 | - | TBC | PRO-PID-38 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | Wellpad LCP (LCP2-2) Separated Water | 10CP520 | Wellpad LCP (LCP2-2) | TBC | Wika 72039876+14503369+0731277 | - |  |  |  | 15 | 0 to 60 | - | Pressure Gauge |  | 0330NDB10CP520 | - | TBC | PRO-PID-38 | 0 | bar(g) | bar(g) | MVar1: 0; MVar2: 15; MVar3: 30; MVar4: 45; MVar5: 60; IdO1: 0; IdO2: 15; IdO3: 30; IdO4: 45; IdO5: 60
Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping | 10-CT510 | TH26 Two Phase Pipeline | TBC | Wika 72039934+72039931 | - |  |  |  | 215 | 0 to 250 | - | - |  | L070NDA10-CT510 | - | TBC | PRO-PID-34 | TH26-4.5.001-01 | °C | °C | MVar1: 0; MVar2: 62.5; MVar3: 125; MVar4: 187.5; MVar5: 250; IdO1: 0; IdO2: 62.5; IdO3: 125; IdO4: 187.5; IdO5: 250
Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water | 10CP011 | SWG Pipeline to TH29 Wellpad | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 15 | -1 to 55 | 0 to 50 | - |  | L210NDB10CP011 | - | TBC | PRO-PID-32 | 0 | bar(g) | mA | MVar1: 0; MVar2: 12.5; MVar3: 25; MVar4: 37.5; MVar5: 50; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Wellpad LCP Common Steam/Water Dump | 10CL010 | Wellpad LCP | TBC | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - |  |  |  | - | 0 to 6000 | 0 to 6000 | - |  | LCP0LFC10CL010 | - | TBC | PRO-PID-38 | 0 | mm | mA | MVar1: 0; MVar2: 1500; MVar3: 3000; MVar4: 4500; MVar5: 6000; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Pump Station Raw Water | 20CP020 | Pump Station | TBC | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - |  |  |  | 3.49 | 0 to 25 | - | - |  | S020GAC20CP020 | - | TBC | PRO-PID-51 | 0 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Production Piping | 20CR004 | Separation Plant | TBC | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - |  |  |  | * | * | * | - |  | S020NDA20CR004 | - | TBC | PRO-PID-14 | TAS4-104-01 | mm/Time Unit | - | MVar1: 0; MVar2: 0; MVar3: 0; MVar4: 0; MVar5: 0; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -
Tauhara B Steamfield | TH11 Building Temp Building Services | 10CT010 | TH11 Building Temp | TBC | RTD PT100 | - |  |  |  | - | 0 to 100 | - | - |  | 0110SAA10CT010 | - | TBC | - | TH11-7.5-002-01 | deg C | mA | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH12 Building Temp Building Services | 10CT010 | TH12 Building Temp | TBC | RTD PT100 | - |  |  |  | - | 0 to 100 | - | - |  | 0120SAA10CT010 | - | TBC | - | TH12-8.5-003-01 | deg C | mA | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH26 Building Temp Building Services | 10CT010 | TH26 Building Temp | TBC | RTD PT100 | - |  |  |  | - | 0 to 100 | - | - |  | 0260SAA10CT010 | - | TBC | - | TH26-4.5-003-01 | deg C | mA | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH28 Building Temp Building Services | 10CT010 | TH28 Building Temp | TBC | RTD PT100 | - |  |  |  | - | 0 to 100 | - | - |  | 0280SAA10CT010 | - | TBC | - | TH28-9.5-003-01 | deg C | mA | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH29 Building Temp Building Services | 10CT010 | TH29 Building Temp | TBC | RTD PT100 | - |  |  |  | - | 0 to 100 | - | - |  | 0290SAA10CT010 | - | TBC | - | TH29-2.5-004-01 | deg C | mA | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | TH37 Building Temp Building Services | 10CT010 | TH37 Building Temp | TBC | RTD PT100 | - |  |  |  | - | 0 to 100 | - | - |  | 0370SAA10CT010 | - | TBC | - | TAS1-3.5-004-01 | deg C | mA | MVar1: 0; MVar2: 25; MVar3: 50; MVar4: 75; MVar5: 100; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | SIS PLC Cabinet TAS4 24Vdc System DCS Power Supplies | 40CE101 | SIS PLC Cabinet TAS4 24Vdc System | Alarm & Indication | TBC | - |  |  |  | - | 0 to 50 | - | - |  | S020CRJ40CE101 | - | TBC | - | TAS4-105-01 | V | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | SIS PLC Cabinet TAS4 Cluster 24VDC DCS Power Supplies | 40CE102 | SIS PLC Cabinet TAS4 Cluster 24VDC | TBC | TBC | - |  |  |  | - | 0 to 50 | - | - |  | S020CRJ40CE102 | - | TBC | - | TAS4-105-01 | V | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | 0 GFHP PUMP SEAL WATER SYSTEM | 21CP512 | 0 | TBC | TBC | - |  |  |  | - | - | - | - |  | P020GWB21CP512 | - | TBC | TABG-JEC-0-000-PRO-PID-0056 | - | - | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | 0 GFHP PUMP SEAL WATER SYSTEM | 22CP512 | 0 | TBC | TBC | - |  |  |  | - | - | - | - |  | P020GWB22CP512 | - | TBC | TABG-JEC-0-000-PRO-PID-0056 | - | - | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CF010 | Separation Plant | Trip & Alarm & Indication | TBC | - |  |  |  | - | 0 to 10 | 0 to 10 | - |  | S020GWA11CF010 | - | TBC | TABG-JEC-0-000-PRO-PID-0055 | TAS2-304-01 | l/m | mA | 0 | 2.5 | 5 | 7.5 | 10 |  |  | 4 | 8 | 12 | 16 | 20 |  |  | 8.5 | 8.7 |  | 7
Tauhara B Steamfield | Acid Dosing Seal Water Flushing Circuit B Flow Acid Dosing Seal Water | 10CF020 | Acid Dosing Seal Water Flushing Circuit B Flow | Trip & Alarm & Indication | TBC | - |  |  |  | - | Vendor supplied | - | - |  | S020GWA11CF020 | - | TBC | TABG-JEC-0-000-PRO-PID-0055 | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - |  |  | 8.5 | 8.7 |  | 7
Tauhara B Steamfield | Acid Dosing Seal Water Cooler B Outlet Temp 0 | 12CT020 | Acid Dosing Seal Water Cooler B Outlet Temp | Alarm & Indication | TBC | - |  |  |  | - | - | - | - |  | S020GWA12CT020 | - | TBC | TABG-JEC-0-000-PRO-PID-0055 | - | - | - | MVar1: -; MVar2: -; MVar3: -; MVar4: -; MVar5: -; IdO1: -; IdO2: -; IdO3: -; IdO4: -; IdO5: -; Digi1: 40
Tauhara B Steamfield | 0 0 | 10CP010 | 0 | TBC | TBC | - |  |  |  | - | - | - | - |  | S020GWA10CP010 | - | TBC | TABG-JEC-0-000-PRO-PID-0055 | - | - | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP011 | Separation Plant | TBC | TBC | - |  |  |  | - | 0 to 25 | 0 to 25 | - |  | S020GWA10CP011 | - | TBC | TABG-JEC-0-000-PRO-PID-0055 | TAS2-304-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP012 | Separation Plant | TBC | TBC | - |  |  |  | - | 0 to 25 | 0 to 25 | - |  | S020GWA10CP012 | - | TBC | TABG-JEC-0-000-PRO-PID-0055 | TAS2-304-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | 0 0 | 10CP020 | 0 | TBC | TBC | - |  |  |  | - | - | - | - |  | S020GWA10CP020 | - | TBC | TABG-JEC-0-000-PRO-PID-0055 | - | - | - | bar: MVar1 to MVar5; IdO1 to IdO5
Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP021 | Separation Plant | TBC | TBC | - |  |  |  | - | 0 to 25 | 0 to 25 | - |  | S020GWA10CP021 | - | TBC | TABG-JEC-0-000-PRO-PID-0055 | TAS2-304-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP022 | Separation Plant | TBC | TBC | - |  |  |  | - | 0 to 25 | 0 to 25 | - |  | S020GWA10CP022 | - | TBC | TABG-JEC-0-000-PRO-PID-0055 | TAS2-304-01 | bar(g) | mA | MVar1: 0; MVar2: 6.25; MVar3: 12.5; MVar4: 18.75; MVar5: 25; IdO1: 4; IdO2: 8; IdO3: 12; IdO4: 16; IdO5: 20
-
-
-
-
-
-
-
-
CCI-DAT-1461
CCI-DAT-1460
CCI-DAT-1460
CCI-DAT-1460
CCI-DAT-1460
CCI-DAT-1463
CCI-DAT-1461
CCI-DAT-1468
CCI-DAT-1460
COSASCO
Model 3500/3500HT
ER-420
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-